## Table 1
Solar Inverter
Modbus Interface Definitions (V2.0)
Issue 01 Date 2020-07-28
HUAWEI TECHNOLOGIES CO., LTD.
Copyright © Huawei Technologies Co., Ltd. 2020. All rights reserved. No part of this document may be reproduced or transmitted in any form or by any means without prior written consent of Huawei Technologies Co., Ltd.
Trademarks and Permissions
and other Huawei trademarks are trademarks of Huawei Technologies Co., Ltd. All other trademarks and trade names mentioned in this document are the property of their respective holders.
Notice The purchased products, services and features are stipulated by the contract made between Huawei and the customer. All or part of the products, services and features described in this document may not be within the purchase scope or the usage scope. Unless otherwise specified in the contract, all statements, information, and recommendations in this document are provided "AS IS" without warranties, guarantees or representations of any kind, either express or implied.
The information in this document is subject to change without notice. Every effort has been made in the preparation of this document to ensure accuracy of the contents, but all statements, information, and recommendations in this document do not constitute a warranty of any kind, express or implied.
Huawei Technologies Co., Ltd. Address: Huawei Industrial Base Bantian, Longgang Shenzhen 518129 People's Republic of China Website: https://e.huawei.com
Contents
1 Supported Models 1 1.1 Model Description. 1 2 Overview. 4 2.1 Terms and Abbreviations 4 3 Register Definitions 6 4 Interface Instructions 20 4.1 Alarm Information 20 4.2 Power Grid Scheduling 24 4.2.1 Active Power Adjustment 24 4.2.1.1 Disabling Active Power Limitation 25 4.2.1.2 Communication Limit by Percentage 25 4.2.1.3 Communication Limit by Fixed Value 26 4.2.1.4 Parameter Setting by Percentage 26 4.2.1.5 Parameter Setting by Fixed Value 27 4.2.2 Reactive Power Adjustment 27 4.2.2.1 Disabling Reactive Power Output 28 4.2.2.2 Communication Adjustment Power Factor 28 4.2.2.3 Communication Adjustment Q/S 29 4.2.2.4 Parameter Setting Power Factor 29 4.2.2.5 Parameter Setting Q/S 30 4.2.3 Curve Adjustment 30 4.2.3.1 cosφ-P/Pn Characteristic Curve 30 4.2.3.2 Q-U Characteristic Curve 31 4.2.3.3 PF-U Characteristic Curve 32 4.3 Grid Codes. 33 4.4 Energy Storage Specifications 43 5 Overview of the Communications Protocol 46 5.1 Physical Layer. 46 5.2 Data Link Layer 46 5.2.1 Modbus-RTU 47 5.2.1.1 ADU Length 47 5.2.1.2 Communications Address 47
5.2.1.3 CRC 47 5.2.2 Modbus-TCP 48 5.2.2.1 ADU Length 48 5.2.2.2 MBAP Packet Header 49 5.2.2.3 Communications Address 50 5.2.2.4 TCP Port 50 5.2.2.5 TCP Link Establishment Process 50 5.3 Application Layer. 51 5.3.1 Function Code List 51 5.3.2 Exception Code List 51 5.3.3 Reading Registers (0x03) 53 5.3.3.1 Frame Format of a Request from a Master Node 53 5.3.3.2 Frame Format of a Normal Response from a Slave Node 53 5.3.3.3 Frame Format of an Abnormal Response from a Slave Node 53 5.3.3.4 Examples 53 5.3.4 Writing a Single Register (0x06) 55 5.3.4.1 Frame Format of a Request from a Master Node 55 5.3.4.2 Frame Format of a Normal Response from a Slave Node 55 5.3.4.3 Frame Format of an Abnormal Response from a Slave Node 55 5.3.4.4 Examples 56 5.3.5 Writing Multiple Registers (0x10) 57 5.3.5.1 Frame Format of a Request from a Master Node 57 5.3.5.2 Frame Format of a Normal Response from a Slave Node 58 5.3.5.3 Frame Format of an Abnormal Response from a Slave Node 58 5.3.5.4 Examples 58 5.3.6 Reading Device Identifiers (0x2B) 60 5.3.6.1 Command for Querying Device Identifiers 61 5.3.6.2 Command for Querying a Device List 62 5.3.6.3 Device Description Definition 63 5.3.7 Huawei-defined Functions (0x41) 64 5.3.7.1 Uploading Files 64 5.3.7.1.1 Starting the Upload 65 5.3.7.1.2 Uploading Data 66 5.3.7.1.3 Completing the Data Upload 67 5.3.7.1.4 Timeout Processing 68
1 Supported Models
This chapter describes the solar inverter models that use the Modbus protocol and the earliest firmware version. When a host needs to connect to these solar inverters, ensure that the firmware version is correct. 1.1 Model Description 1.1 Model Description
Table 1-1 Supported models and firmware versions
Model | Mo del ID | Earliest Firm Version | Pmax (kW) | Qmax (kVar) | Smax (kVA) | Pn (kW) | Num ber of PV Strin gs
SUN2000-8KTL | 5 | SUN2000 V100R001C81 | 8.8 | 5.28 | 8.8 | 8 | 4
SUN2000-10KTL | 4 | SUN2000 V100R001C81 | 11 | 6.6 | 11 | 10 | 4
SUN2000-12KTL | 3 | SUN2000 V100R001C81 | 13.2 | 7.92 | 13.2 | 12 | 4
SUN2000-15KTL | 2 | SUN2000 V100R001C81 | 16.5 | 9.9 | 16.5 | 15 | 6
SUN2000-17KTL | 1 | SUN2000 V100R001C81 | 18.7 | 11.22 | 18.7 | 17 | 6
SUN2000-20KTL | 0 | SUN2000 V100R001C81 | 22 | 13.2 | 22 | 20 | 6
SUN2000-22KTL-US | 25 | SUN2000 V200R001C02 | 22.2 | 14.64 | 24.4 | 22.2 | 6
SUN2000-23KTL | 17 | SUN2000 V100R001C81 | 23 | 13.8 | 23 | 23 | 6
SUN2000-24.5KTL | 16 | SUN2000 V100R001C81 | 24.5 | 14.7 | 24.5 | 24.5 | 6
SUN2000-24.7KTL- JP | 32 | SUN2000 V200R002C00 | 24.7 | 15 | 25 | 24.7 | 8
SUN2000-25KTL-US | 21 | SUN2000 V200R001C02 | 25 | 16.5 | 27.5 | 25 | 6
SUN2000-28KTL | 18 | SUN2000 V100R001C81 | 27.5 | 16.5 | 27.5 | 27.5 | 6
SUN2000-29.9KTL | 60 | SUN2000 V200R002C00 | 29.9 | 17.94 | 29.9 | 29.9 | 8
SUN2000-30KTL-US | 22 | SUN2000 V200R001C02 | 30 | 19.8 | 33 | 30 | 6
SUN2000-30KTL-A | 23 | SUN2000 V200R001C90 | 30 | 19.8 | 33 | 30 | 6
SUN2000-33KTL | 19 | SUN2000 V200R001C90 | 33 | 19.8 | 33 | 30 | 6
SUN2000-33KTL-A | 43 | SUN2000 V200R002C00 | 33 | 19.8 | 33 | 30 | 8
SUN2000-33KTL- E001 | 44 | SUN2000 V200R001C90 | 30 | 19.8 | 33 | 30 | 6
SUN2000-33KTL-JP | 28 | SUN2000 V200R002C00 | 33.3 | 22.8 | 38 | 33.3 | 8
SUN2000-33KTL-US | 36 | SUN2000 V200R002C20 | 36.6 | 21.96 | 36.6 | 33.3 | 8
SUN2000-40KTL | 20 | SUN2000 V200R001C90 | 40 | 24 | 40 | 36 | 6
SUN2000-36KTL | 27 | SUN2000 V200R002C00 | 40 | 24 | 40 | 36 | 8
SUN2000-36KTL-US | 37 | SUN2000 V200R002C20 | 40 | 24 | 40 | 36 | 8
SUN2000-40KTL-JP | 29 | SUN2000 V200R002C00 | 40 | 27.6 | 46 | 40 | 8
SUN2000-40KTL-US | 35 | SUN2000 V200R002C20 | 44 | 26.4 | 44 | 40 | 8
SUN2000-42KTL | 26 | SUN2000 V200R002C00 | 47 | 28.2 | 47 | 42 | 8
SUN2000-43KTL- IN-C1 | 31 | SUN2000 V200R002C00 | 52.5 | 31.5 | 52.5 | 43 | 8
SUN2000-45KTL- US-HV-D0 | 34 | SUN2000HA V100R001C00 | 50 | 30 | 50 | 45 | 8
SUN2000-50KTL | 30 | SUN2000 V200R002C00 | 50.5 | 30.3 | 50.5 | 46 | 8
SUN2000-50KTL-C1 | 24 | SUN2000 V200R002C00 | 52.5 | 31.5 | 52.5 | 47.5 | 8
SUN2000-55KTL- HV-D1 | 38 | SUN2000HA V100R001C00 | 60 | 36 | 60 | 55 | 8
SUN2000-55KTL- IN-HV-D1 | 39 | SUN2000HA V100R001C00 | 66 | 39.6 | 66 | 55 | 8
SUN2000-55KTL- HV-D1-001 | 40 | SUN2000HA V100R001C00 | 66 | 39.6 | 66 | 55 | 8
SUN2000-60KTL- HV-D1 | 33 | SUN2000HA V100R001C00 | 66 | 39.6 | 66 | 60 | 8
SUN2000-60KTL- HV-D1-001 | 41 | SUN2000HA V100R001C00 | 66 | 39.6 | 66 | 60 | 8
NOTE The maximum active power (Pmax), maximum reactive power (Qmax), maximum apparent power (Smax), and rated power (Pn) of each model are for reference only. For details, see the corresponding model specifications.

## Table 2
2 Overview
Modbus is a widely used protocol for device communications. This document describes the Modbus protocol used by Huawei solar inverters, and can be used to regulate follow-up third-party integrated development. Huawei solar inverters comply with the standard Modbus protocol, and this document focuses on the information specific to Huawei solar inverters. For other information about Modbus, see the standard documents about the Modbus protocol. For details about the standard protocols used by Huawei solar inverters and customized interaction modes and examples, see Communications Protocol Overview. 2.1 Terms and Abbreviations 2.1 Terms and Abbreviations
Table 2-1 Terms and abbreviations
Name | Description
Master node | During master-slave communication, the party that initiates a communication request is referred to as the master node.
Slave node | During master-slave communication, the party that responds to a communication request is referred to as the slave node.
Broadcast address | Fixed to 0.
Register address | A register address is recorded in two bytes.
U16 | Unsigned integer (16 bits)
U32 | Unsigned integer (32 bits)
I16 | Signed integer (16 bits)
I32 | Signed integer (32 bits)
STR | Character string
MLD | Multiple bytes
Bitfield16 | 16-bit data expressed by bit
Bitfield32 | 32-bit data expressed by bit
N/A | Not applicable
s | Second
Epoch seconds | The number of seconds that have elapsed since 1970-01-01 00:00:00
RO | Data that is readable only
RW | Data that is readable and writable
WO | Data that is writable only

## Table 3
3 Register Definitions
Table 3-1 Register definitions
No. | Signal Name | Read/ Write | Type | Uni t | Gai n | Addr ess | Qu ant ity | Scope
1 | Model ID | RO | U16 | N/ A | 1 | 3200 1 | 1 | N/A
2 | Output mode | RO | U16 | N/ A | 1 | 3200 2 | 1 | N/A
3 | SN | RO | STR | N/ A | 1 | 3200 3 | 10 | N/A
4 | PN | RO | STR | N/ A | 1 | 3215 3 | 10 | N/A
5 | System time | RO | EPOCH TIME | N/ A | 1 | 3220 0 | 2 | N/A
6 | PV1 voltage | RO | I16 | V | 10 | 3226 2 | 1 | N/A
7 | PV1 current | RO | I16 | A | 10 | 3226 3 | 1 | N/A
8 | PV2 voltage | RO | I16 | V | 10 | 3226 4 | 1 | N/A
9 | PV2 current | RO | I16 | A | 10 | 3226 5 | 1 | N/A
10 | PV3 voltage | RO | I16 | V | 10 | 3226 6 | 1 | N/A
11 | PV3 current | RO | I16 | A | 10 | 3226 7 | 1 | N/A
12 | PV4 voltage | RO | I16 | V | 10 | 3226 8 | 1 | N/A
13 | PV4 current | RO | I16 | A | 10 | 3226 9 | 1 | N/A
14 | PV5 voltage | RO | I16 | V | 10 | 3227 0 | 1 | N/A
15 | PV5 current | RO | I16 | A | 10 | 3227 1 | 1 | N/A
16 | PV6 voltage | RO | I16 | V | 10 | 3227 2 | 1 | N/A
17 | PV6 current | RO | I16 | A | 10 | 3227 3 | 1 | N/A
18 | Line voltage between phases A and B | RO | U16 | V | 10 | 3227 4 | 1 | N/A
19 | Line voltage between phases B and C | RO | U16 | V | 10 | 3227 5 | 1 | N/A
20 | Line voltage between phases C and A | RO | U16 | V | 10 | 3227 6 | 1 | N/A
21 | Phase A voltage | RO | U16 | V | 10 | 3227 7 | 1 | N/A
22 | Phase B voltage | RO | U16 | V | 10 | 3227 8 | 1 | N/A
23 | Phase C voltage | RO | U16 | V | 10 | 3227 9 | 1 | N/A
24 | Phase A current | RO | U16 | A | 10 | 3228 0 | 1 | N/A
25 | Phase B current | RO | U16 | A | 10 | 3228 1 | 1 | N/A
26 | Phase C current | RO | U16 | A | 10 | 3228 2 | 1 | N/A
27 | Grid frequency | RO | U16 | Hz | 100 | 3228 3 | 1 | N/A
28 | Power factor | RO | I16 | N/ A | 100 0 | 3228 4 | 1 | N/A
29 | Inverter efficiency | RO | U16 | % | 100 | 3228 5 | 1 | N/A
30 | Internal temperature | RO | I16 | °C | 10 | 3228 6 | 1 | N/A
31 | Device status | RO | U16 | N/ A | 1 | 3228 7 | 1 | N/A
32 | Peak active power of current day | RO | I32 | kW | 100 0 | 3228 8 | 2 | N/A
33 | Active power | RO | I32 | kW | 100 0 | 3229 0 | 2 | N/A
34 | Reactive power | RO | I32 | kVa r | 100 0 | 3229 2 | 2 | N/A
35 | Input power | RO | U32 | kW | 100 0 | 3229 4 | 2 | N/A
36 | Current energy yield collection time | RO | EPOCH TIME | N/ A | 1 | 3229 6 | 2 | N/A
37 | Energy yield in current hour | RO | U32 | kW h | 100 | 3229 8 | 2 | N/A
38 | Daily energy yield | RO | U32 | kW h | 100 | 3230 0 | 2 | N/A
39 | Monthly energy yield | RO | U32 | kW h | 100 | 3230 2 | 2 | N/A
40 | Annual energy yield | RO | U32 | kW h | 100 | 3230 4 | 2 | N/A
41 | Accumulated energy yield | RO | U32 | kW h | 100 | 3230 6 | 2 | N/A
42 | PV7 voltage | RO | I16 | V | 10 | 3231 4 | 1 | N/A
43 | PV7 current | RO | I16 | A | 10 | 3231 5 | 1 | N/A
44 | PV8 voltage | RO | I16 | V | 10 | 3231 6 | 1 | N/A
45 | PV8 current | RO | I16 | A | 10 | 3231 7 | 1 | N/A
46 | State 1 | RO | Bitfield 16 | N/ A | 1 | 3231 9 | 1 | Bit 0: standby Bit 1: grid-connected Bit 2: grid-connected normally Bit 3: grid connection with derating due to power rationing Bit 4: grid connection with derating due to internal causes of the solar inverter Bit 5: normal stop Bit 6: stop due to faults Bit 7: stop due to power rationing Bit 8: shutdown Bit 9: spot check
47 | State 2 | RO | Bitfield 16 | N/ A | 1 | 3232 0 | 1 | Bit 0: locking status (0: locked; 1: unlocked)
48 | State 3 | RO | Bitfield 16 | N/ A | 1 | 3232 1 | 1 | Bit 0: ZVRT protection Bit 1: LVRT protection Bit 2: anti-islanding protection
49 | State 4 | RO | Bitfield 16 | N/ A | 1 | 3232 2 | 1 | Bit 0: grid-connected Bit 1: grid-connected (compatible and reserved)
50 | Insulation resistance | RO | U16 | M Ω | 100 0 | 3232 3 | 1 | N/A
51 | Startup time | RO | EPOCH TIME | s | 1 | 3232 5 | 2 | N/A
52 | Shutdown time | RO | EPOCH TIME | s | 1 | 3232 7 | 2 | N/A
53 | Energy yield collection time for previous hour | RO | EPOCH TIME | N/ A | 1 | 3234 3 | 2 | N/A
54 | Energy yield in previous hour | RO | U32 | kW h | 100 | 3234 5 | 2 | N/A
55 | Energy yield collection time for previous day | RO | EPOCH TIME | N/ A | 1 | 3234 7 | 2 | N/A
56 | Energy yield on previous day | RO | U32 | kW h | 100 | 3234 9 | 2 | N/A
57 | Energy yield collection time for previous month | RO | EPOCH TIME | N/ A | 1 | 3235 1 | 2 | N/A
58 | Energy yield in previous month | RO | U32 | kW h | 100 | 3235 3 | 2 | N/A
59 | Energy yield collection time for previous year | RO | EPOCH TIME | N/ A | 1 | 3235 5 | 2 | N/A
60 | Energy yield in previous year | RO | U32 | kW h | 100 | 3235 7 | 2 | N/A
61 | [Active] Adjustment mode | RO | U16 | N/ A | 1 | 3240 2 | 1 | 0: percentage 1: fixed value NOTICE Addresses 32402 to 32405 need to be read at a time.
62 | [Active] Adjustment value | RO | U32 | N/ A | * | 3240 3 | 2 | Percentage: 0.1% Fixed value: 0.001 kW NOTICE For details about the adjustment value precision, see the corresponding adjustment command precision.
63 | [Active] Adjustment command | RO | U16 | N/ A | 1 | 3240 5 | 1 | 42320: active power derating by percentage (local) 40125: active power derating by percentage (0.1%) 40119: active power derating by percentage (1%) 40232: command for active power derating by percentage (0.1%) 40234: command for active power derating by percentage (1%) 42332: local active power derating by fixed value 40120: active power derating by fixed value 40235: command for active power derating by fixed value 42178: maximum active power
64 | [Reactive] Adjustment mode | RO | U16 | N/ A | 1 | 3240 6 | 1 | 0: power factor 1: absolute value 2: Q/S 3: Q-U characteristic curve (command ID: 0) 4: cosφ-P/Pn characteristic curve (command ID: 0) 5: PF-U characteristic curve (command ID: 0) 6: Q-P characteristic curve (command ID: 0) NOTICE Addresses 32406 to 32409 need to be read at a time.
65 | [Reactive] Adjustment value | RO | U32 | N/ A | * | 3240 7 | 2 | Power factor: 0.001 Absolute value: 0.001 kVar Q/S: 0.001 Q-U characteristic curve: 0 cosφ-P/Pn characteristic curve: 0 PF-U characteristic curve: 0 Q-P characteristic curve: 0 NOTICE For details about the adjustment value precision, see the corresponding adjustment command precision.
66 | [Reactive] Adjustment command | RO | U16 | N/ A | 1 | 3240 9 | 1 | 42321: local power factor adjustment 40122: power factor adjustment 40237: power factor command 40129: reactive power compensation at night (kVar) 40123: Q/S adjustment 40236: Q/S command 42809: reactive power compensation at night (Q/S)
67 | MPPT1 total input power | RO | U32 | kW | 100 0 | 3302 2 | 2 | N/A
68 | MPPT2 total input power | RO | U32 | kW | 100 0 | 3302 4 | 2 | N/A
69 | MPPT3 total input power | RO | U32 | kW | 100 0 | 3302 6 | 2 | N/A
70 | MPPT4 total input power | RO | U32 | kW | 100 0 | 3307 0 | 2 | N/A
71 | System time | RW | EPOCH TIME | N/ A | 1 | 4000 0 | 2 | [946684800, 3155759999] Epoch seconds, local time
72 | [Power grid scheduling] Reactive power compensation mode | RW | U16 | N/ A | 1 | 4011 7 | 1 | [0, 8] NOTICE Stores data but does not support high-frequency write operations.
73 | [Power grid scheduling] Active power control mode | RW | U16 | N/ A | 1 | 4011 8 | 1 | [0, 4] NOTICE Stores data but does not support high-frequency write operations.
74 | [Power grid scheduling] Active power percentage derating (1%) | RW | U16 | % | 1 | 4011 9 | 1 | [0, 100] NOTICE Stores data but does not support high-frequency write operations.
75 | [Power grid scheduling] Fixed active power derated | RW | U16 | kW | 10 | 4012 0 | 1 | [0, Pmax] NOTICE Stores data but does not support high-frequency write operations.
76 | [Power grid scheduling] Active power change gradient | RW | U16 | %/s | 10 | 4012 1 | 1 | [0.1, 1000]* NOTICE Stores data but does not support high-frequency write operations.
77 | [Power grid scheduling] Reactive power compensation (PF) | RW | I16 | N/ A | 100 0 | 4012 2 | 1 | (–1, –0.8]U[0.8, 1] NOTICE Stores data but does not support high-frequency write operations.
78 | [Power grid scheduling] Reactive power compensation (Q/S) | RW | I16 | N/ A | 100 0 | 4012 3 | 1 | [–1, 1] NOTICE Stores data but does not support high-frequency write operations.
79 | [Power grid scheduling] Reactive power adjustment time | RW | U16 | s | 1 | 4012 4 | 1 | [1, 1000] NOTICE Stores data but does not support high-frequency write operations.
80 | [Power grid scheduling] Active power percentage derating (0.1%) | RW | U16 | % | 10 | 4012 5 | 1 | [0,100] NOTICE Stores data but does not support high-frequency write operations.
81 | [Power grid scheduling] cosφ-P/Pn characteristic curve | RW | BYTES | N/ A | 1 | 4013 3 | 21 | N/A
82 | [Power grid scheduling] Q- U characteristic curve | RW | BYTES | N/ A | 1 | 4015 4 | 21 | N/A
83 | [Power grid scheduling] Q- U power percentage to exit scheduling | RW | U16 | % | 1 | 4019 8 | 1 | [0, 100]
84 | Startup | WO | U16 | N/ A | 1 | 4020 0 | 1 | N/A
85 | Shutdown | WO | U16 | N/ A | 1 | 4020 1 | 1 | N/A
86 | [Power grid scheduling] Active power percentage derating command (0.1%) | WO | U16 | % | 10 | 4023 2 | 1 | [0, 100] Supports high-frequency write operations but does not store data.
87 | [Power grid scheduling] Fixed active power derating command (1%) | WO | U16 | % | 1 | 4023 4 | 1 | [0, 100] Supports high-frequency write operations but does not store data.
88 | [Power grid scheduling] Fixed active power derating command | WO | U16 | kW | 10 | 4023 5 | 1 | [0, Pmax] Supports high-frequency write operations but does not store data.
89 | [Power grid scheduling] Reactive power compensation command (Q/S) | WO | I16 | N/ A | 100 0 | 4023 6 | 1 | [–1, 1] Supports high-frequency write operations but does not store data.
90 | [Power grid scheduling] Reactive power compensation command (PF) | WO | I16 | N/ A | 100 0 | 4023 7 | 1 | (–1, –0.8]U[0.8, 1] Supports high-frequency write operations but does not store data.
91 | Level-1 OV protection time | RW | U32 | ms | 1 | 4204 5 | 2 | [50, 7200000]*
92 | Level-2 OV protection time | RW | U32 | ms | 1 | 4204 7 | 2 | [50, 7200000]*
93 | Level-1 UV protection time | RW | U32 | ms | 1 | 4204 9 | 2 | [50, 7200000]*
94 | Level-2 UV protection time | RW | U32 | ms | 1 | 4205 1 | 2 | [50, 7200000]*
95 | Level-1 OF protection time | RW | U32 | ms | 1 | 4205 3 | 2 | [50, 7200000]*
96 | Level-2 OF protection time | RW | U32 | ms | 1 | 4205 5 | 2 | [50, 7200000]*
97 | Level-1 UF protection time | RW | U32 | ms | 1 | 4205 7 | 2 | [50, 7200000]*
98 | Level-2 UF protection time | RW | U32 | ms | 1 | 4205 9 | 2 | [50, 7200000]*
99 | 10-minute OV protection time | RW | U32 | ms | 1 | 4206 1 | 2 | [50, 7200000]*
100 | Level-1 OV protection | RW | U16 | V | 10 | 4206 3 | 1 | [1 x Vn, 1.36 x Vn]
101 | Level-2 OV protection | RW | U16 | V | 10 | 4206 4 | 1 | [1 x Vn, 1.36 x Vn]
102 | Level-1 UV protection | RW | U16 | V | 10 | 4206 5 | 1 | [0.15 x Vn, 1 x Vn]
103 | Level-2 UV protection | RW | U16 | V | 10 | 4206 6 | 1 | [0.15 x Vn, 1 x Vn]
104 | Level-1 OF protection | RW | U16 | Hz | 100 | 4206 7 | 1 | [1 x Fn, 1.15 x Fn]
105 | Level-2 OF protection | RW | U16 | Hz | 100 | 4206 8 | 1 | [1 x Fn, 1.15 x Fn]
106 | Level-1 UF protection | RW | U16 | Hz | 100 | 4206 9 | 1 | [0.85 x Fn, 1 x Fn]
107 | Level-2 UF protection | RW | U16 | Hz | 100 | 4207 0 | 1 | [0.85 x Fn, 1 x Fn]
108 | 10 minute OV protection | RW | U16 | V | 10 | 4207 1 | 1 | [1 x Vn, 1.36 x Vn]
109 | Grid code | RW | U16 | N/ A | 1 | 4207 2 | 1 | [0, 93]
110 | Insulation resistance protection | RW | U16 | M Ω | 100 0 | 4207 4 | 1 | [0.033, 1.5]*
111 | Unbalance voltage protection | RW | U16 | % | 10 | 4207 5 | 1 | [0, 50]
112 | Soft start time after grid failure | RW | U16 | s | 1 | 4208 3 | 1 | [20, 800]
113 | LVRT | RW | U16 | N/ A | 1 | 4208 4 | 1 | 0: disable 1: enable
114 | Soft start time | RW | U16 | s | 1 | 4208 5 | 1 | [20, 1800]
115 | Grid connection duration after grid recovery | RW | U16 | s | 1 | 4208 6 | 1 | [0, 7200]
116 | Active islanding protection | RW | U16 | N/ A | 1 | 4208 7 | 1 | 0: disable 1: enable
117 | LVRT reactive power compensation power factor | RW | U16 | N/ A | 10 | 4208 9 | 1 | [0, 10]
118 | Reactive power compensation (cosφ-P) trigger voltage | RW | U16 | % | 1 | 4209 0 | 1 | [100, 110]
119 | Reactive power compensation (cosφ-P) exit voltage | RW | U16 | % | 1 | 4209 1 | 1 | [90, 100]
120 | Trigger frequency of overfrequency derating | RW | U16 | Hz | 100 | 4209 2 | 1 | 50 Hz: [45, 55) 60 Hz: [55, 65)
121 | Quit frequency of overfrequency derating | RW | U16 | Hz | 100 | 4209 3 | 1 | 50 Hz: [45, 55) 60 Hz: [55, 65)
122 | Power recovery gradient of overfrequency derating | RW | U16 | %/ mi n | 1 | 4209 4 | 1 | [1, 6000]
123 | Q-U characteristic curve mode | RW | U16 | N/ A | 1 | 4209 5 | 1 | [0, 1]
124 | Q-U scheduling trigger power percent | RW | U16 | % | 1 | 4209 6 | 1 | [0, 100]
125 | MPPT multi- peak scanning | RW | U16 | N/ A | 1 | 4209 7 | 1 | [0, 1]
126 | MPPT scanning interval | RW | U16 | mi n | 1 | 4210 1 | 1 | [5, 30]
127 | AFCI | RW | U16 | NA | 1 | 4212 5 | 1 | [0, 1]
128 | Level-3 OV protection | RW | U16 | V | 10 | 4215 1 | 1 | [1 x Vn, 1.36 x Vn]
129 | Level-3 OV protection time | RW | U32 | ms | 1 | 4215 2 | 2 | [50, 7200000]*
130 | Level-4 OV protection | RW | U16 | V | 10 | 4215 4 | 1 | [1 x Vn, 1.36 x Vn]
131 | Level-4 OV protection time | RW | U32 | ms | 1 | 4215 5 | 2 | [50, 7200000]*
132 | Level-3 UV protection | RW | U16 | V | 10 | 4215 7 | 1 | [0.15 x Vn, 1 x Vn]
133 | Level-3 UV protection time | RW | U32 | ms | 1 | 4215 8 | 2 | [50, 7200000]*
134 | Level-4 UV protection | RW | U16 | V | 10 | 4216 0 | 1 | [0.15 x Vn, 1 x Vn]
135 | Level-4 UV protection time | RW | U32 | ms | 1 | 4216 1 | 2 | [50, 7200000]*
136 | Shutdown at 0% power limit | RW | U16 | N/ A | 1 | 4217 4 | 1 | [0, 1]
137 | System time: year | RW | U16 | N/ A | 1 | 4230 0 | 1 | [2000, 2069]
138 | System time: month | RW | U16 | N/ A | 1 | 4230 1 | 1 | [1, 12]
139 | System time: day | RW | U16 | N/ A | 1 | 4230 2 | 1 | [1, 31]
140 | System time: hour | RW | U16 | N/ A | 1 | 4230 3 | 1 | [0, 23]
141 | System time: minute | RW | U16 | N/ A | 1 | 4230 4 | 1 | [0, 59]
142 | System time: second | RW | U16 | N/ A | 1 | 4230 5 | 1 | [0, 59]
143 | [Power grid scheduling] Active power percentage derating | RW | U16 | % | 1 | 4232 0 | 1 | [0, 100]
144 | [Power grid scheduling] Power factor | RW | I16 | N/ A | 100 0 | 4232 1 | 1 | (–1, –0.8]U[0.8, 1]
145 | Remote power scheduling | RW | U16 | N/ A | 1 | 4233 3 | 1 | 0: disable 1: enable
146 | AFCI self check | WO | U16 | N/ A | 1 | 4273 1 | 1 | N/A
147 | Alarm 1 | RO | Bitfield 16 | N/ A | 1 | 5000 0 | 1 | N/A
148 | Alarm 2 | RO | Bitfield 16 | N/ A | 1 | 5000 1 | 1 | N/A
149 | Alarm 3 | RO | Bitfield 16 | N/ A | 1 | 5000 2 | 1 | N/A
150 | Alarm 4 | RO | Bitfield 16 | N/ A | 1 | 5000 3 | 1 | N/A
151 | Alarm 5 | RO | Bitfield 16 | N/ A | 1 | 5000 4 | 1 | N/A
152 | Alarm 6 | RO | Bitfield 16 | N/ A | 1 | 5000 5 | 1 | N/A
153 | Alarm 7 | RO | Bitfield 16 | N/ A | 1 | 5000 6 | 1 | N/A
154 | Alarm 8 | RO | Bitfield 16 | N/ A | 1 | 5000 7 | 1 | N/A
155 | Alarm 9 | RO | Bitfield 16 | N/ A | 1 | 5000 8 | 1 | N/A
156 | Alarm 10 | RO | Bitfield 16 | N/ A | 1 | 5000 9 | 1 | N/A
157 | Alarm 11 | RO | Bitfield 16 | N/ A | 1 | 5001 0 | 1 | N/A
158 | Alarm 12 | RO | Bitfield 16 | N/ A | 1 | 5001 1 | 1 | N/A
159 | Alarm 13 | RO | Bitfield 16 | N/ A | 1 | 5001 2 | 1 | N/A
160 | Alarm 14 | RO | Bitfield 16 | N/ A | 1 | 5001 3 | 1 | N/A
161 | Alarm 15 | RO | Bitfield 16 | N/ A | 1 | 5001 4 | 1 | N/A
162 | Alarm 16 | RO | Bitfield 16 | N/ A | 1 | 5001 5 | 1 | N/A
163 | Alarm 17 | RO | Bitfield 16 | N/ A | 1 | 5001 6 | 1 | N/A
NOTICE
For some models, ranges marked with * may be wider than the actual ranges. The interface result code prevails.

## Table 4
4 Interface Instructions
4.1 Alarm Information 4.2 Power Grid Scheduling 4.3 Grid Codes 4.4 Energy Storage Specifications 4.1 Alarm Information
Table 4-1 Alarm information
No. | Alarm | Bit | Alarm Name | Alarm ID | Cause ID | Level
1 | 50000 | 1 | Abnormal String 1 | 106 | 1 | Warning
2 | 50000 | 2 | Abnormal String 2 | 107 | 1 | Warning
3 | 50000 | 3 | Abnormal String 3 | 108 | 1 | Warning
4 | 50000 | 4 | Abnormal String 4 | 109 | 1 | Warning
5 | 50000 | 5 | Abnormal String 5 | 110 | 1 | Warning
6 | 50000 | 6 | Abnormal String 6 | 111 | 1 | Warning
7 | 50000 | 10 | Software Ver. Unmatch | 504 | 1 | Minor
8 | 50000 | 12 | Upgrade Failed | 505 | 1 | Major
9 | 50000 | 13 | Flash Fault | 61440 | 1 | Minor
10 | 50000 | 14 | License Expired | 506 | 1 | Warning
11 | 50001 | 1 | Software Ver. Unmatch | 504 | 2 | Minor
12 | 50001 | 2 | Software Ver. Unmatch | 504 | 3 | Minor
13 | 50001 | 3 | System Fault | 400 | 1 | Major
14 | 50001 | 4 | System Fault | 400 | 27 | Major
15 | 50001 | 5 | Abnormal DC Circuit | 200 | 16 | Major
16 | 50001 | 6 | Abnormal Inv. Circuit | 202 | 20 | Major
17 | 50001 | 7 | Abn. Residual Curr. | 318 | 1 | Major
18 | 50001 | 8 | Overtemperature | 321 | 1 | Major
19 | 50001 | 10 | System Fault | 400 | 28 | Major
20 | 50001 | 11 | Fan Fault | 320 | 1 | Minor
21 | 50001 | 12 | Abnormal SPI Comm. | 322 | 1 | Major
22 | 50001 | 14 | System Fault | 400 | 29 | Major
23 | 50002 | 0 | Low Insulation Resistance | 313 | 1 | Major
24 | 50002 | 1 | AFCI Self-Check Failure | 411 | 1 | Major
25 | 50002 | 2 | DC Arc Fault | 412 | 1 | Major
26 | 50002 | 3 | AFCI Self-Check Failure | 411 | 2 | Major
27 | 50002 | 4 | AFCI Self-Check Failure | 411 | 3 | Major
28 | 50002 | 5 | Abnormal Inv. Circuit | 202 | 21 | Major
29 | 50002 | 7 | System Fault | 400 | 30 | Major
30 | 50002 | 8 | System Fault | 400 | 31 | Major
31 | 50002 | 9 | String 3 Reversed | 122 | 1 | Major
32 | 50002 | 12 | DC Arc Fault | 412 | 2 | Major
33 | 50002 | 13 | DC Arc Fault | 412 | 3 | Major
34 | 50002 | 14 | DC Arc Fault | 412 | 4 | Major
35 | 50002 | 15 | System Fault | 400 | 23 | Major
36 | 50003 | 1 | String 1 Reversed | 120 | 1 | Major
37 | 50003 | 2 | String 2 Reversed | 121 | 1 | Major
38 | 50003 | 3 | Abnormal DC Circuit | 200 | 12 | Major
39 | 50003 | 6 | String 4 Reversed | 123 | 1 | Major
40 | 50003 | 7 | String 5 Reversed | 124 | 1 | Major
41 | 50003 | 8 | String 6 Reversed | 125 | 1 | Major
42 | 50003 | 9 | High DC Input Voltage | 103 | 1 | Major
43 | 50003 | 10 | High DC Input Voltage | 103 | 2 | Major
44 | 50003 | 11 | High DC Input Voltage | 103 | 3 | Major
45 | 50003 | 12 | High DC Input Voltage | 103 | 4 | Major
46 | 50003 | 15 | Abnormal DC Circuit | 200 | 15 | Major
47 | 50004 | 2 | String 1 Reversed | 120 | 2 | Warning
48 | 50004 | 3 | String 2 Reversed | 121 | 2 | Warning
49 | 50004 | 4 | String 7 Reversed | 126 | 1 | Major
50 | 50004 | 5 | String 7 Reversed | 126 | 2 | Warning
51 | 50004 | 6 | String 8 Reversed | 127 | 1 | Major
52 | 50004 | 7 | String 8 Reversed | 127 | 2 | Warning
53 | 50004 | 8 | Abnormal PV String Connection | 413 | 1 | Major
54 | 50004 | 9 | Abnormal PV String Connection | 413 | 2 | Major
55 | 50004 | 10 | Abnormal PV String Connection | 413 | 3 | Major
56 | 50004 | 11 | Abnormal PV String Connection | 413 | 4 | Major
57 | 50004 | 12 | String 3 Reversed | 122 | 2 | Warning
58 | 50004 | 13 | String 4 Reversed | 123 | 2 | Warning
59 | 50004 | 14 | String 5 Reversed | 124 | 2 | Warning
60 | 50004 | 15 | String 6 Reversed | 125 | 2 | Warning
61 | 50005 | 1 | Abnormal DC Circuit | 200 | 3 | Major
62 | 50005 | 2 | Abn. Auxiliary Power | 410 | 4 | Major
63 | 50005 | 4 | Abnormal DC Circuit | 200 | 10 | Major
64 | 50005 | 5 | Abnormal DC Circuit | 200 | 11 | Major
65 | 50005 | 6 | Abnormal DC Circuit | 200 | 30 | Major
66 | 50005 | 7 | BST Inductor Cable Connection Abnormal | 414 | 1 | Major
67 | 50005 | 8 | BST Inductor Cable Connection Abnormal | 414 | 2 | Major
68 | 50005 | 9 | BST Inductor Cable Connection Abnormal | 414 | 3 | Major
69 | 50005 | 10 | BST Inductor Cable Connection Abnormal | 414 | 4 | Major
70 | 50006 | 6 | System Fault | 400 | 3 | Major
71 | 50006 | 10 | Abnormal Inv. Circuit | 202 | 13 | Major
72 | 50006 | 12 | Abnormal Inv. Circuit | 202 | 14 | Major
73 | 50007 | 1 | Abnormal Inv. Circuit | 202 | 16 | Major
74 | 50007 | 5 | System Fault | 400 | 21 | Major
75 | 50008 | 0 | Abnormal Grid Voltage | 301 | 4 | Major
76 | 50008 | 3 | Abnormal Grid Voltage | 301 | 16 | Major
77 | 50008 | 6 | Abnormal Grid Frequency | 305 | 2 | Major
78 | 50008 | 7 | Abnormal Grid Frequency | 305 | 4 | Major
79 | 50008 | 8 | Abnormal Grid Voltage | 301 | 28 | Major
80 | 50008 | 9 | Abnormal Grid Voltage | 301 | 29 | Major
81 | 50008 | 10 | Abnormal Grounding | 326 | 1 | Major
82 | 50008 | 11 | Abnormal Grid Voltage | 301 | 26 | Major
83 | 50008 | 12 | Abnormal Grid Frequency | 305 | 5 | Major
84 | 50009 | 0 | Abnormal Grid Voltage | 301 | 31 | Major
85 | 50009 | 1 | Abnormal Grid Voltage | 301 | 32 | Major
86 | 50009 | 2 | Abnormal Grid Voltage | 301 | 33 | Major
87 | 50009 | 8 | Abnormal Grid Voltage | 301 | 19 | Major
88 | 50016 | 0 | Abnormal String 1 | 106 | 1 | Warning
89 | 50016 | 1 | Abnormal String 2 | 107 | 1 | Warning
90 | 50016 | 2 | Abnormal String 3 | 108 | 1 | Warning
91 | 50016 | 3 | Abnormal String 4 | 109 | 1 | Warning
92 | 50016 | 4 | Abnormal String 5 | 110 | 1 | Warning
93 | 50016 | 5 | Abnormal String 6 | 111 | 1 | Warning
94 | 50016 | 6 | Abnormal String 7 | 112 | 1 | Warning
95 | 50016 | 7 | Abnormal String 8 | 113 | 1 | Warning

## Table 5
4.2 Power Grid Scheduling This section describes the active power adjustment, reactive power adjustment, and curve configuration formats and precautions for power grid curve scheduling. 4.2.1 Active Power Adjustment The solar inverter provides five active power adjustment modes. The active power adjustment response speed can be modified by setting Active power derating gradient (register 40121).
Table 4-2 Signal information for active power adjustment
No. | Signal Name | Re ad/ Wri te | Type | Unit | Gain | Addr ess | Quan tity | Restraints
1 | Active power | RW | U16 | N/A | 1 | 4011 | 1 | Stores data but does
| control mode |  |  |  |  | 8 |  | not support high-
frequency write operations.
2 | Active power percentage | RW | U16 | % | 1 | 4011 9 | 1
derating (1%)
3 | Fixed active power | RW | U16 | kW | 10 | 4012 | 1
| derating |  |  |  |  | 0

## Table 6
No. | Signal Name | Re ad/ Wri te | Type | Unit | Gain | Addr ess | Quan tity | Restraints
4 | Active power | RW | U16 | %/s | 10 | 4012 | 1
| change gradient |  |  |  |  | 1
5 | Active power | RW | U16 | % | 10 | 4012 | 1
| percentage |  |  |  |  | 5
derating (0.1%)
6 | Active power | WO | U16 | % | 10 | 4023 | 1 | Supports high-
| percentage |  |  |  |  | 2 |  | frequency write
| derating command | [6 empty] | operations but does not
| (0.1%) | [6 empty] | store data.
7 | Active power | WO | U16 | % | 1 | 4023 | 1
| percentage |  |  |  |  | 4
derating command
(1%)
8 | Fixed active power | WO | U16 | kW | 10 | 4023 | 1
| derating command |  |  |  |  | 5
NOTE
● If a storage interface that needs to be written frequently is required, ensure that the solar inverter version is V100R001C81SPC107, V200R001C00SPC106, or a later version. ● If the Fixed active power derating command interface is required, ensure that the solar inverter version is V100R001C81SPC107, V200R001C00SPC106, or a later version.
4.2.1.1 Disabling Active Power Limitation The solar inverter does not accept any derating command. It can run with power up to Pmax. Other register interfaces are not required. Operation: Set Active power control (register 40118) to 0.
NOTE
After the mode of Active power control (register 40118) is changed, the solar inverter automatically saves the register value. You do not need to write the value repeatedly. If you need to send a value periodically, send the value at intervals greater than 12 minutes.
4.2.1.2 Communication Limit by Percentage The solar inverter switches to remote control mode and receives the active power derating command in percentage. The reference value of the percentage is the reported Pmax. Pmax varies depending on the solar inverter model. For details, see 1.1 Model Description.
Operation: ● Scenario in which the derating precision is 1%: Change the value of Active power control (register 40118) to 1, and change the value of Active power percentage derating command (1%) (register 40234) to the target value (%). ● Scenario in which the derating precision is 0.1%: Change the value of Active power control (register 40118) to 1, and change the value of Active power percentage derating command (0.1%) (register 40232) to the target value (%).
NOTE
● After the mode of Active power control (register 40118) is changed, the solar inverter automatically saves the register value. You do not need to write the value repeatedly. If you need to send a value periodically, send the value at intervals greater than 12 minutes. ● Active power percentage derating command (1%) (register 40234) and Active power percentage derating command (0.1%) (register 40232) need to be sent by the host periodically at intervals no more than 10 minutes. Otherwise, the solar inverter will automatically restore the active output to 100% of Pmax. The solar inverter does not save the derating command set in this mode. After the solar inverter is powered on again, the power is restored to 100% of Pmax.
4.2.1.3 Communication Limit by Fixed Value The solar inverter switches to remote control mode. It receives the active derating command in the form of a fixed value measured in kW. The adjustment precision is 0.1 kW. The maximum value is Pmax of the solar inverter, and the minimum value is 0. Operation: Change the value of Active power control (register 40118) to 4, and then change the value of Fixed active power derating (register 40235) to the target value (kW).
NOTE
● After the mode of Active power control (register 40118) is changed, the solar inverter automatically saves the register value. You do not need to write the value repeatedly. If you need to send a value periodically, send the value at intervals greater than 12 minutes. ● Fixed active power derating (register 40235) needs to be sent by the host at intervals no more than 10 minutes. Otherwise, the inverter will automatically restore active power output to 100% of Pmax. The solar inverter does not save the derating command set in this mode. After the solar inverter is powered on again, the power is restored to 100% of Pmax.
4.2.1.4 Parameter Setting by Percentage The host sends an active power derating command in percentage. The reference value of the percentage is the reported Pmax. Pmax varies depending on the solar inverter model. For details, see 1.1 Model Description. Operation:
● Scenario in which the derating precision is 1%: Change the value of Active power control (register 40118) to 3, and change the value of Active power percentage derating command (1%) (register 40119) to the target value (%). ● Scenario in which the derating precision is 0.1%: Change the value of Active power control (register 40118) to 3, and change the value of Active power percentage derating command (0.1%) (register 40125) to the target value (%). NOTE

## Table 7
● After the mode of Active power control (register 40118) is changed, the solar inverter automatically saves the register value. You do not need to write the value repeatedly. If you need to send a value periodically, send the value at intervals greater than 12 minutes. ● After Active power percentage derating (1%) (register 40119) or Active power percentage derating (0.1%) (register 40125) is set, the solar inverter applies and saves the setting. The value does not need to be sent periodically. If you need to send a value periodically, send the value at intervals greater than 12 minutes.
4.2.1.5 Parameter Setting by Fixed Value The host delivers the active scheduling target value, which is an absolute value measured in kW. The adjustment precision is 0.1 kW. The maximum value is the reported Pmax, and the minimum value is 0. Operation: Change the value of Active power control (register 40118) to 2, and then change the value of Fixed active power derating (register 40120) to the target value (kW).
NOTE
● After the mode of Active power control (register 40118) is changed, the solar inverter automatically saves the register value. You do not need to write the value repeatedly. If you need to send a value periodically, send the value at intervals greater than 12 minutes. ● After Fixed active power derating (register 40120) is set, the solar inverter applies and saves the setting. The value does not need to be sent periodically. If you need to send a value periodically, send the value at intervals greater than 12 minutes. 4.2.2 Reactive Power Adjustment The solar inverter provides multiple reactive power adjustment modes. The reactive power adjustment response speed can be modified by setting Reactive power adjustment time (register 40124).
Table 4-3 Signal information for reactive power adjustment
No. | Signal Name | Read / Writ e | Type | Unit | Gain | Addre ss | Qua ntity | Restraints
1 | Reactive power compensation | RW | U16 | N/A | 1 | 40117 | 1 | Stores data but does not support high-

## Table 8
No. | Signal Name | Read / Writ e | Type | Unit | Gain | Addre ss | Qua ntity | Restraints
2 | Reactive power compensation (PF) | RW | I16 | N/A | 1000 | 40122 | 1 | frequency write operations.
3 | Reactive power compensation (Q/S) | RW | I16 | N/A | 1000 | 40123 | 1
4 | Reactive power adjustment time | RW | U16 | s | 1 | 40124 | 1
5 | Reactive power compensation command (Q/S) | WO | I16 | N/A | 1000 | 40236 | 1 | Supports high- frequency write operations but does not store data.
6 | Reactive power compensation command (PF) | WO | I16 | N/A | 1000 | 40237 | 1
NOTE
● If a storage interface that needs to be written frequently is required, ensure that the solar inverter version is V100R001C81SPC107, V200R001C00SPC106, or a later version. ● If the Reactive power compensation command (Q/S) interface is required, ensure that the solar inverter version is V100R001C81SPC107, V200R001C00SPC106, or a later version. 4.2.2.1 Disabling Reactive Power Output The solar inverter does not provide reactive power. The on-grid power factor is 1. Additional register interfaces are not required. Operation: Change the value of Reactive power control (register 40117) to 0.
NOTE
After the mode of Reactive power control (register 40117) is changed, the solar inverter automatically saves the register value. You do not need to write the value repeatedly. If you need to send a value periodically, send the value at intervals greater than 12 minutes. 4.2.2.2 Communication Adjustment Power Factor The solar inverter switches to remote control mode and receives the reactive power derating command in the form of a power factor. Operation:
Change the value of Reactive power control (register 40117) to 1 and then change the value of Reactive power compensation command (PF) (register 40237) to the target value for power adjustment.
NOTE
● After the mode of Reactive power control (register 40117) is changed, the solar inverter automatically saves the register value. You do not need to write the value repeatedly. If you need to send a value periodically, send the value at intervals greater than 12 minutes. ● Reactive power compensation (PF) (register 40237) needs to be sent by the host at intervals no more than 10 minutes. Otherwise, the solar inverter will automatically disable reactive power output.
4.2.2.3 Communication Adjustment Q/S The solar inverter switches to remote control mode and receives the reactive power adjustment command in the form of Q/S. Operation: Change the value of Reactive power control (register 40117) to 6 and then change the value of Reactive power compensation command (Q/S) (register 40236) to the target value for power adjustment.
NOTE
● After the mode of Reactive power control (register 40117) is changed, the solar inverter automatically saves the register value. You do not need to write the value repeatedly. If you need to send a value periodically, send the value at intervals greater than 12 minutes. ● Reactive power compensation command (Q/S) (register 40236) needs to be sent by the host at intervals no more than 10 minutes. Otherwise, the solar inverter will automatically disable reactive power output.
4.2.2.4 Parameter Setting Power Factor The host sends a reactive power adjustment command in the form of a power factor. The output reactive power of the solar inverter is related to the output active power. Operation: Change the value of Reactive power control (register 40117) to 3 and then change the value of Reactive power compensation (PF) (register 40122) to the target value for power adjustment.
NOTE
● After the mode of Reactive power control (register 40117) is changed, the solar inverter automatically saves the register value. You do not need to write the value repeatedly. If you need to send a value periodically, send the value at intervals greater than 12 minutes. ● After Reactive power compensation (PF) (register 40122) is set, the solar inverter applies and saves the setting. The value does not need to be sent periodically. If you need to send a value periodically, send the value at intervals greater than 12 minutes.
4.2.2.5 Parameter Setting Q/S The host sends a reactive power adjustment command in the form of Q/S. Q is the reactive power target value (kVar), and S is the maximum apparent power of the solar inverter (kVA). For details about the maximum apparent power of different models, see the signal definition table. Operation: Change the value of Reactive power control (register 40117) to 2 and then change the value of Reactive power compensation (Q/S) (register 40123) to the target value for power adjustment.

## Table 9
NOTE
● After the mode of Reactive power control (register 40117) is changed, the solar inverter automatically saves the register value. You do not need to write the value repeatedly. If you need to send a value periodically, send the value at intervals greater than 12 minutes. ● After Reactive power compensation (Q/S) (register 40123) is set, the solar inverter applies and saves the setting. The value does not need to be sent periodically. If you need to send a value periodically, send the value at intervals greater than 12 minutes. 4.2.3 Curve Adjustment
4.2.3.1 cosφ-P/Pn Characteristic Curve
Table 4-4 cosφ-P/Pn characteristic curve definition
Description | Data Type | Gain | Unit | Value Range
Number of points | U16 | 1 | N/A | [2, 10]
P/Pn value at point 1 | U16 | 10 | % | [0, 100]
cosφ value at point 1 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/Pn value at point 2 | U16 | 10 | % | [0, 100]
cosφ value at point 2 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/Pn value at point 3 | U16 | 10 | % | [0, 100]
cosφ value at point 3 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/Pn value at point 4 | U16 | 10 | % | [0, 100]
cosφ value at point 4 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/Pn value at point 5 | U16 | 10 | % | [0, 100]
cosφ value at point 5 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/Pn value at point 6 | U16 | 10 | % | [0, 100]
cosφ value at point 6 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/Pn value at point 7 | U16 | 10 | % | [0, 100]
cosφ value at point 7 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/Pn value at point 8 | U16 | 10 | % | [0, 100]
cosφ value at point 8 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/Pn value at point 9 | U16 | 10 | % | [0, 100]
cosφ value at point 9 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
P/Pn value at point 10 | U16 | 10 | % | [0, 100]
cosφ value at point 10 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]

## Table 10
4.2.3.2 Q-U Characteristic Curve
Table 4-5 Q-U characteristic curve definition
Description | Data Type | Gain | Unit | Value Range
Number of points | U16 | 1 | N/A | [2, 10]
U/Un value at point 1 | U16 | 10 | % | [80, 136]
Q/S value at point 1 | I16 | 1000 | N/A | [–0.6, 0.6]
U/Un value at point 2 | U16 | 10 | % | [80, 136]
Q/S value at point 2 | I16 | 1000 | N/A | [–0.6, 0.6]
U/Un value at point 3 | U16 | 10 | % | [80, 136]
Q/S value at point 3 | I16 | 1000 | N/A | [–0.6, 0.6]
U/Un value at point 4 | U16 | 10 | % | [80, 136]
Q/S value at point 4 | I16 | 1000 | N/A | [–0.6, 0.6]
U/Un value at point 5 | U16 | 10 | % | [80, 136]
Q/S value at point 5 | I16 | 1000 | N/A | [–0.6, 0.6]
U/Un value at point 6 | U16 | 10 | % | [80, 136]
Q/S value at point 6 | I16 | 1000 | N/A | [–0.6, 0.6]
U/Un value at point 7 | U16 | 10 | % | [80, 136]

## Table 11
Description | Data Type | Gain | Unit | Value Range
Q/S value at point 7 | I16 | 1000 | N/A | [–0.6, 0.6]
U/Un value at point 8 | U16 | 10 | % | [80, 136]
Q/S value at point 8 | I16 | 1000 | N/A | [–0.6, 0.6]
U/Un value at point 9 | U16 | 10 | % | [80, 136]
Q/S value at point 9 | I16 | 1000 | N/A | [–0.6, 0.6]
U/Un value at point 10 | U16 | 10 | % | [80, 136]
Q/S value at point 10 | I16 | 1000 | N/A | [–0.6, 0.6]
NOTICE
In Italian standards, this curve may be used together with the Q-U characteristic curve mode, Q-U dispatch trigger power (%), and Q-U power percentage to exit scheduling parameters.
4.2.3.3 PF-U Characteristic Curve
Table 4-6 PF-U characteristic curve definition
Description | Data Type | Gain | Unit | Value Range
Number of points | U16 | 1 | N/A | [2, 10]
U/Un value at point 1 | U16 | 10 | % | [80, 136]
PF value at point 1 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/Un value at point 2 | U16 | 10 | % | [80, 136]
PF value at point 2 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/Un value at point 3 | U16 | 10 | % | [80, 136]
PF value at point 3 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/Un value at point 4 | U16 | 10 | % | [80, 136]
PF value at point 4 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/Un value at point 5 | U16 | 10 | % | [80, 136]
PF value at point 5 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/Un value at point 6 | U16 | 10 | % | [80, 136]
Description | Data Type | Gain | Unit | Value Range
PF value at point 6 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/Un value at point 7 | U16 | 10 | % | [80, 136]
PF value at point 7 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/Un value at point 8 | U16 | 10 | % | [80, 136]
PF value at point 8 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/Un value at point 9 | U16 | 10 | % | [80, 136]
PF value at point 9 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]
U/Un value at point 10 | U16 | 10 | % | [80, 136]
PF value at point 10 | I16 | 1000 | N/A | (–1, –0.8]U[0.8, 1]

## Table 12
4.3 Grid Codes
Table 4-7 List of grid codes
No. | Standard | Applicable Country or Region
0 | VDE-AR-N-4105 | Germany
1 | NB/T 32004 | China
2 | UTE C 15-712-1(A) | France
3 | UTE C 15-712-1(B) | France
4 | UTE C 15-712-1(C) | France
5 | VDE 0126-1-1-BU | Bulgaria
6 | VDE 0126-1-1-GR(A) | Greece
7 | VDE 0126-1-1-GR(B) | Greece
8 | BDEW-MV | Germany
9 | G59-England | UK
10 | G59-Scotland | UK
11 | G83-England | UK
12 | G83-Scotland | UK
13 | CEI0-21 | Italy
14 | EN50438-CZ | Czech Republic
15 | RD1699/661 | Spain
16 | RD1699/661-MV480 | Spain
17 | EN50438-NL | Netherlands
18 | C10/11 | Belgium
19 | AS4777 | Australia
20 | IEC61727 | General
21 | Custom (50 Hz) | Custom
22 | Custom (60 Hz) | Custom
23 | CEI0-16 | Italy
24 | CHINA-MV480 | China
25 | CHINA-MV | China
26 | TAI-PEA | Thailand
27 | TAI-MEA | Thailand
28 | BDEW-MV480 | Germany
29 | Custom MV480 (50 Hz) | Custom
30 | Custom MV480 (60 Hz) | Custom
31 | G59-England-MV480 | UK
32 | IEC61727-MV480 | General
33 | UTE C 15-712-1-MV480 | France
34 | TAI-PEA-MV480 | Thailand
35 | TAI-MEA-MV480 | Thailand
36 | EN50438-DK-MV480 | Denmark
37 | Japan standard (50 Hz) | Japan
38 | Japan standard (60 Hz) | Japan
39 | EN50438-TR-MV480 | Turkey
40 | EN50438-TR | Turkey
41 | C11/C10-MV480 | Belgium
42 | Philippines | Philippines
43 | Philippines-MV480 | Philippines
44 | AS4777-MV480 | Australia
45 | NRS-097-2-1 | South Africa
46 | NRS-097-2-1-MV480 | South Africa
47 | KOREA | South Korea
48 | IEEE 1547-MV480 | USA
49 | IEC61727-60Hz | General
50 | IEC61727-60Hz-MV480 | General
51 | CHINA_MV500 | China
52 | ANRE | Romania
53 | ANRE-MV480 | Romania
54 | ELECTRIC RULE NO.21-MV480 | California, USA
55 | HECO-MV480 | Hawaii, USA
56 | PRC_024_Eastern-MV480 | Eastern USA
57 | PRC_024_Western-MV480 | Western USA
58 | PRC_024_Quebec-MV480 | Quebec, Canada
59 | PRC_024_ERCOT-MV480 | Texas, USA
60 | PO12.3-MV480 | Spain
61 | EN50438_IE-MV480 | Ireland
62 | EN50438_IE | Ireland
63 | IEEE 1547a-MV480 | USA
64 | Japan standard (MV420-50 Hz) | Japan
65 | Japan standard (MV420-60 Hz) | Japan
66 | Japan standard (MV440-50 Hz) | Japan
67 | Japan standard (MV440-60 Hz) | Japan
68 | IEC61727-50Hz-MV500 | General
70 | CEI0-16-MV480 | Italy
71 | PO12.3 | Spain
72 | Japan standard (MV400-50 Hz) | Japan
73 | Japan standard (MV400-60 Hz) | Japan
74 | CEI0-21-MV480 | Italy
75 | KOREA-MV480 | South Korea
76 | Egypt ETEC | Egypt
77 | Egypt ETEC-MV480 | Egypt
78 | CHINA_MV800 | China
79 | IEEE 1547-MV600 | USA
80 | ELECTRIC RULE NO.21-MV600 | California, USA
81 | HECO-MV600 | Hawaii, USA
82 | PRC_024_Eastern-MV600 | Eastern USA
83 | PRC_024_Western-MV600 | Western USA
84 | PRC_024_Quebec-MV600 | Quebec, Canada
85 | PRC_024_ERCOT-MV600 | Texas, USA
86 | IEEE 1547a-MV600 | USA
87 | EN50549-LV | Ireland
88 | EN50549-MV480 | Ireland
89 | Jordan-Transmission | Jordan
90 | Jordan-Transmission-MV480 | Jordan
91 | NAMIBIA | Namibia
92 | ABNT NBR 16149 | Brazil
93 | ABNT NBR 16149-MV480 | Brazil
94 | SA_RPPs | South Africa
95 | SA_RPPs-MV480 | South Africa
96 | INDIA | India
97 | INDIA-MV500 | India
98 | ZAMBIA | Zambia
99 | ZAMBIA-MV480 | Zambia
100 | Chile | Chile
101 | Chile-MV480 | Chile
102 | CHINA-MV500-STD | China
103 | CHINA-MV480-STD | China
104 | Mexico-MV480 | Mexico
105 | Malaysian | Malaysia
106 | Malaysian-MV480 | Malaysia
107 | KENYA_ETHIOPIA | East Africa
108 | KENYA_ETHIOPIA-MV480 | East Africa
109 | G59-England-MV800 | UK
110 | NIGERIA | Nigeria
111 | NIGERIA-MV480 | Nigeria
112 | DUBAI | Dubai
113 | DUBAI-MV480 | Dubai
114 | Northern Ireland | Northern Ireland
115 | Northern Ireland-MV480 | Northern Ireland
116 | Cameroon | Cameroon
117 | Cameroon-MV480 | Cameroon
118 | Jordan-Distribution | Jordan
119 | Jordan-Distribution-MV480 | Jordan
120 | Custom-MV600-50Hz | Custom
121 | AS4777-MV800 | Australia
122 | INDIA-MV800 | India
123 | IEC61727-MV800 | General
124 | BDEW-MV800 | Germany
125 | ABNT NBR 16149-MV800 | Brazil
126 | UTE C 15-712-1-MV800 | France
127 | Chile-MV800 | Chile
128 | Mexico-MV800 | Mexico
129 | EN50438-TR-MV800 | Turkey
130 | TAI-PEA-MV800 | Thailand
131 | Philippines-MV800 | Philippines
132 | Malaysian-MV800 | Malaysia
133 | NRS-097-2-1-MV800 | South Africa
134 | SA_RPPs-MV800 | South Africa
135 | Jordan-Transmission-MV800 | Jordan
136 | Jordan-Distribution-MV800 | Jordan
137 | Egypt ETEC-MV800 | Egypt
138 | DUBAI-MV800 | Dubai
139 | SAUDI-MV800 | Saudi Arabia
140 | EN50438_IE-MV800 | Ireland
141 | EN50549-MV800 | Ireland
142 | Northern Ireland-MV800 | Northern Ireland
143 | CEI0-21-MV800 | Italy
144 | IEC 61727-MV800-60Hz | General
145 | NAMIBIA_MV480 | Namibia
146 | Japan (LV202-50 Hz) | Japan
147 | Japan (LV202-60 Hz) | Japan
148 | Pakistan-MV800 | Pakistan
149 | BRASIL-ANEEL-MV800 | Brazil
150 | Israel-MV800 | Israel
151 | CEI0-16-MV800 | Italy
152 | ZAMBIA-MV800 | Zambia
153 | KENYA_ETHIOPIA-MV800 | East Africa
154 | NAMIBIA_MV800 | Namibia
155 | Cameroon-MV800 | Cameroon
156 | NIGERIA-MV800 | Nigeria
157 | ABUDHABI-MV800 | Abu Dhabi
158 | LEBANON | Lebanon
159 | LEBANON-MV480 | Lebanon
160 | LEBANON-MV800 | Lebanon
161 | ARGENTINA-MV800 | Argentina
162 | ARGENTINA-MV500 | Argentina
163 | Jordan-Transmission-HV | Jordan
164 | Jordan-Transmission-HV480 | Jordan
165 | Jordan-Transmission-HV800 | Jordan
166 | TUNISIA | Tunisia
167 | TUNISIA-MV480 | Tunisia
168 | TUNISIA-MV800 | Tunisia
169 | JAMAICA-MV800 | Jamaica
170 | AUSTRALIA-NER | Australia
171 | AUSTRALIA-NER-MV480 | Australia
172 | AUSTRALIA-NER-MV800 | Australia
173 | SAUDI | Saudi Arabia
174 | SAUDI-MV480 | Saudi Arabia
175 | Ghana-MV480 | Ghana
176 | Israel | Israel
177 | Israel-MV480 | Israel
178 | Chile-PMGD | Chile
179 | Chile-PMGD-MV480 | Chile
180 | VDE-AR-N4120-HV | Germany
181 | VDE-AR-N4120-HV480 | Germany
182 | VDE-AR-N4120-HV800 | Germany
183 | IEEE 1547-MV800 | USA
184 | Nicaragua-MV800 | Nicaragua
185 | IEEE 1547a-MV800 | USA
186 | ELECTRIC RULE NO.21-MV800 | California, USA
187 | HECO-MV800 | Hawaii, USA
188 | PRC_024_Eastern-MV800 | Eastern USA
189 | PRC_024_Western-MV800 | Western USA
190 | PRC_024_Quebec-MV800 | Quebec, Canada
191 | PRC_024_ERCOT-MV800 | Texas, USA
192 | Custom-MV800-50Hz | Custom
193 | RD1699/661-MV800 | Spain
194 | PO12.3-MV800 | Spain
195 | Mexico-MV600 | Mexico
196 | Vietnam-MV800 | Vietnam
197 | CHINA-LV220/380 | China
198 | SVG-LV | Dedicated
199 | Vietnam | Vietnam
200 | Vietnam-MV480 | Vietnam
201 | Chile-PMGD-MV800 | Chile
202 | Ghana-MV800 | Ghana
203 | TAIPOWER | Taiwan
204 | TAIPOWER-MV480 | Taiwan
205 | TAIPOWER-MV800 | Taiwan
206 | IEEE 1547-LV208 | USA
207 | IEEE 1547-LV240 | USA
208 | IEEE 1547a-LV208 | USA
209 | IEEE 1547a-LV240 | USA
210 | ELECTRIC RULE NO.21-LV208 | USA
211 | ELECTRIC RULE NO.21-LV240 | USA
212 | HECO-O+M+H-LV208 | USA
213 | HECO-O+M+H-LV240 | USA
214 | PRC_024_Eastern-LV208 | USA
215 | PRC_024_Eastern-LV240 | USA
216 | PRC_024_Western-LV208 | USA
217 | PRC_024_Western-LV240 | USA
218 | PRC_024_ERCOT-LV208 | USA
219 | PRC_024_ERCOT-LV240 | USA
220 | PRC_024_Quebec-LV208 | USA
221 | PRC_024_Quebec-LV240 | USA
222 | ARGENTINA-MV480 | Argentina
223 | Oman | Oman
224 | Oman-MV480 | Oman
225 | Oman-MV800 | Oman
226 | Kuwait | Kuwait
227 | Kuwait-MV480 | Kuwait
228 | Kuwait-MV800 | Kuwait
229 | Bangladesh | Bangladesh
230 | Bangladesh-MV480 | Bangladesh
231 | Bangladesh-MV800 | Bangladesh
232 | Chile-Net_Billing | Chile
233 | EN50438-NL-MV480 | Netherlands
234 | Bahrain | Bahrain
235 | Bahrain-MV480 | Bahrain
236 | Bahrain-MV800 | Bahrain
238 | Japan-MV550-50Hz | Japan
239 | Japan-MV550-60Hz | Japan
241 | ARGENTINA | Argentina
242 | KAZAKHSTAN-MV800 | Kazakhstan
243 | Mauritius | Mauritius
244 | Mauritius-MV480 | Mauritius
245 | Mauritius-MV800 | Mauritius
246 | Oman-PDO-MV800 | Oman
247 | EN50438-SE | Sweden
248 | TAI-MEA-MV800 | Thailand
249 | Pakistan | Pakistan
250 | Pakistan-MV480 | Pakistan
251 | PORTUGAL-MV800 | Portugal
252 | HECO-L+M-LV208 | USA
253 | HECO-L+M-LV240 | USA
254 | C10/11-MV800 | Belgium
255 | Austria | Austria
256 | Austria-MV480 | Austria
257 | G98 | UK
258 | G99-TYPEA-LV | UK
259 | G99-TYPEB-LV | UK
260 | G99-TYPEB-HV | UK
261 | G99-TYPEB-HV-MV480 | UK
262 | G99-TYPEB-HV-MV800 | UK
263 | G99-TYPEC-HV-MV800 | UK
264 | G99-TYPED-MV800 | UK
265 | G99-TYPEA-HV | UK
266 | CEA-MV800 | India
267 | EN50549-MV400 | Europe
268 | VDE-AR-N4110 | Germany
269 | VDE-AR-N4110-MV480 | Germany
270 | VDE-AR-N4110-MV800 | Germany
271 | Panama-MV800 | Panama
272 | North Macedonia-MV800 | North Macedonia
273 | NTS | Spain
274 | NTS-MV480 | Spain
275 | NTS-MV800 | Spain
NOTICE
Set the grid code based on local laws and regulations.

## Table 13
4.4 Energy Storage Specifications
Table 4-8 Format description of parameters for time-of-use electricity price periods
Description | Data Type | Gain | Unit | Value Range
Number of periods | U16 | 1 | N/A | [0, 10]
Start time of period 1 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 1 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Electricity price in period 1 | U32 | 1000 | N/A | N/A
Start time of period 2 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 2 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Electricity price in period 2 | U32 | 1000 | N/A | N/A
... | ... | ... | ... | ...
Start time of period 10 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 10 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Electricity price in period 10 | U32 | 1000 | N/A | N/A

## Table 14
Table 4-9 Format description of parameters for fixed charging and discharging periods
Description | Data Type | Gai n | Unit | Value Range
Number of periods | U16 | 1 | N/A | [0, 10]
Start time of period 1 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 1 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Charging and discharging power in period 1 | I32 | 1 | W | [Discharging power limit, Charging power limit]. For details, see the description of the supported model.
Start time of period 2 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 2 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Charging and discharging power in period 2 | I32 | 1 | W | [Discharging power limit, Charging power limit]. For details, see the description of the supported model.
... | ... | ... | ... | ...
Start time of period 10 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
End time of period 10 | U16 | 1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
Charging and discharging power in period 10 | I32 | 1 | W | [Discharging power limit, Charging power limit]. For details, see the description of the supported model.
5 Overview of the Communications Protocol
The Modbus communications protocol consists of the following layers.
Figure 5-1 Modbus protocol layers
5.1 Physical Layer 5.2 Data Link Layer 5.3 Application Layer 5.1 Physical Layer Huawei solar inverters provide Modbus communication based on physical media such as MBUS, RS485, WLAN, FE, and 4G. MBUS and RS485 comply with the Modbus-RTU format. The communication through the WLAN, FE, and 4G media is based on the TCP link and complies with the Modbus-TCP format. 5.2 Data Link Layer The following figure shows the generic frame structure of the Modbus protocol.
Figure 5-2 Modbus generic frame format

## Table 15
5.2.1 Modbus-RTU
Figure 5-3 Modbus-RTU frame format
5.2.1.1 ADU Length The application data unit (ADU) consists of 256 bytes based on the serial bus. 1. Slave address: 1 byte 2. Cyclic redundancy check (CRC): 2 bytes 3. PDU: 253 bytes
5.2.1.2 Communications Address As shown in Figure 5-3, Modbus-RTU is usually used for serial communication. Slave address represents the address of a slave solar inverter. The address range is allocated as follows:
Table 5-1 Serial link address allocation
Broadcast Address | Slave Node Address | Reserved Address
0 | 1–247 | 248–255
Reserved addresses are used for access control of the communication extension modules. Huawei reserves the right to allocate the reserved addresses.
5.2.1.3 CRC CRC applies to all bytes in front of the CRC code, which consists of 16 bits. The reference code is as follows:
static unsigned char auchCRCHi[] = { 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01,
0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40, 0x01, 0xC0, 0x80, 0x41, 0x01, 0xC0, 0x80, 0x41, 0x00, 0xC1, 0x81, 0x40 } ; /*CRC values for the low-order byte*/ static char auchCRCLo[] = { 0x00, 0xC0, 0xC1, 0x01, 0xC3, 0x03, 0x02, 0xC2, 0xC6, 0x06, 0x07, 0xC7, 0x05, 0xC5, 0xC4, 0x04, 0xCC, 0x0C, 0x0D, 0xCD, 0x0F, 0xCF, 0xCE, 0x0E, 0x0A, 0xCA, 0xCB, 0x0B, 0xC9, 0x09, 0x08, 0xC8, 0xD8, 0x18, 0x19, 0xD9, 0x1B, 0xDB, 0xDA, 0x1A, 0x1E, 0xDE, 0xDF, 0x1F, 0xDD, 0x1D, 0x1C, 0xDC, 0x14, 0xD4, 0xD5, 0x15, 0xD7, 0x17, 0x16, 0xD6, 0xD2, 0x12, 0x13, 0xD3, 0x11, 0xD1, 0xD0, 0x10, 0xF0, 0x30, 0x31, 0xF1, 0x33, 0xF3, 0xF2, 0x32, 0x36, 0xF6, 0xF7, 0x37, 0xF5, 0x35, 0x34, 0xF4, 0x3C, 0xFC, 0xFD, 0x3D, 0xFF, 0x3F, 0x3E, 0xFE, 0xFA, 0x3A, 0x3B, 0xFB, 0x39, 0xF9, 0xF8, 0x38, 0x28, 0xE8, 0xE9, 0x29, 0xEB, 0x2B, 0x2A, 0xEA, 0xEE, 0x2E, 0x2F, 0xEF, 0x2D, 0xED, 0xEC, 0x2C, 0xE4, 0x24, 0x25, 0xE5, 0x27, 0xE7, 0xE6, 0x26, 0x22, 0xE2, 0xE3, 0x23, 0xE1, 0x21, 0x20, 0xE0, 0xA0, 0x60, 0x61, 0xA1, 0x63, 0xA3, 0xA2, 0x62, 0x66, 0xA6, 0xA7, 0x67, 0xA5, 0x65, 0x64, 0xA4, 0x6C, 0xAC, 0xAD, 0x6D, 0xAF, 0x6F, 0x6E, 0xAE, 0xAA, 0x6A, 0x6B, 0xAB, 0x69, 0xA9, 0xA8, 0x68, 0x78, 0xB8, 0xB9, 0x79, 0xBB, 0x7B, 0x7A, 0xBA, 0xBE, 0x7E, 0x7F, 0xBF, 0x7D, 0xBD, 0xBC, 0x7C, 0xB4, 0x74, 0x75, 0xB5, 0x77, 0xB7, 0xB6, 0x76, 0x72, 0xB2, 0xB3, 0x73, 0xB1, 0x71, 0x70, 0xB0, 0x50, 0x90, 0x91, 0x51, 0x93, 0x53, 0x52, 0x92, 0x96, 0x56, 0x57, 0x97, 0x55, 0x95, 0x94, 0x54, 0x9C, 0x5C, 0x5D, 0x9D, 0x5F, 0x9F, 0x9E, 0x5E, 0x5A, 0x9A, 0x9B, 0x5B, 0x99, 0x59, 0x58, 0x98, 0x88, 0x48, 0x49, 0x89, 0x4B, 0x8B, 0x8A, 0x4A, 0x4E, 0x8E, 0x8F, 0x4F, 0x8D, 0x4D, 0x4C, 0x8C, 0x44, 0x84, 0x85, 0x45, 0x87, 0x47, 0x46, 0x86, 0x82, 0x42, 0x43, 0x83, 0x41, 0x81, 0x80, 0x40 }; unsigned short CRC16 ( puchMsg, usDataLen ) /* The function returns the CRC as a unsigned short type */ unsigned char *puchMsg ; /* message to calculate CRC upon */ unsigned short usDataLen ; /* quantity of bytes in message */ { unsigned char uchCRCHi = 0xFF ; /* high byte of CRC initialized */ unsigned char uchCRCLo = 0xFF ; /* low byte of CRC initialized */ unsigned uIndex ; /* will index into CRC lookup table */ while (usDataLen--) /* pass through message buffer */ { uIndex = uchCRCLo ^ *puchMsg++ ; /* calculate the CRC */ uchCRCLo = uchCRCHi ^ auchCRCHi[uIndex] ; uchCRCHi = auchCRCLo[uIndex] ; } return (uchCRCHi << 8 ¦ uchCRCLo) ; }
Code source: MODBUS over Serial Line Specification and Implementation Guide V1.02 5.2.2 Modbus-TCP
Figure 5-4 Modbus-TCP frame format
5.2.2.1 ADU Length The recommended frame length is 260 bytes based on the standard. When some extended functions are applied, the data service provider may extend the ADU to a proper length based on the resources it possesses, to improve network
transmission efficiency. The ADU length is indicated by the length field in the MBAP packet header. 5.2.2.2 MBAP Packet Header If Modbus is applied to TCP/IP, a dedicated MBAP packet header (Modbus application protocol packet header) is used to identify the Modbus ADU. The Modbus packet header consists of four fields and seven bytes, which are defined as follows.

## Table 16
Table 5-2 MBAP definition
Data Field | Length (Byte) | Description | Client | Server
Transmission | 2 | Matching | Assigned by | The identifier
identifier |  | identifier | the client; | of the
|  | between a | better be | response
|  | request frame | unique for | frame from
|  | and a | each data | the server
|  | response | frame | must be
|  | frame |  | consistent
with that of
the request
frame.
Protocol type | 2 | 0 = Modbus | Assigned by | The identifier
|  | protocol | the client; 0 | of the
|  |  | by default | response
frame from
the server
must be
consistent
with that of
the request
frame.
Data length | 2 | Follow-up | Assigned by | Assigned by
|  | data length | the client | the server
|  |  | based on the | based on the
|  |  | actual data | actual frame
|  |  | frame | length
Logical device | 1 | 0 | Assigned by | The identifier
ID |  |  | the client | of the
|  |  | based on the | response
|  |  | actual data | frame from
|  |  | frame request | the server
must be
consistent
with that of
the request
frame.
5.2.2.3 Communications Address Based on the TCP communications host, unit 0 is used by default to access the directly connected slave node, and other addresses are used to access the downstream devices of the slave node. The default address of the slave node is 0. The address is adjustable.
Figure 5-5 Communications address of the three-layer object structure
5.2.2.4 TCP Port In a local area network or VPN environment, the master node may actively initiate TCP socket link establishment to the slave node. The master node can use the 502 port to request data services from the slave node. In a non-VPN environment across the public network, the device deployed on the internal network needs to initiate TCP socket link establishment to the master node exposed on the public network. In this case, you need to preset the fixed access port number of the master node on the slave node. To ensure security and reduce traffic, the master node must provide at least one encrypted port and one non-encrypted port.
5.2.2.5 TCP Link Establishment Process This section focuses on the cross-public network application. The following figure shows the process of connecting a slave node.

## Table 17
Figure 5-6 Process of establishing a secure TCP connection
5.3 Application Layer 5.3.1 Function Code List
Table 5-3 Function code list
Function Code | Description | Remarks
0x03 | Read registers. | Continuously reads a single register or multiple registers.
0x06 | Write a single register. | Writes into a single register.
0x10 | Write multiple registers. | Continuously writes into multiple registers.
5.3.2 Exception Code List The exception codes must be unique for each network element (NE) type. The names and descriptions should be provided in both the Chinese and English NE
interface document. Different versions of the same NE type must be backward compatible. Exception codes in use cannot be assigned to other exceptions.

## Table 18
Table 5-4 Exception codes returned by an NE (0x00–0x8F are for common exception codes)
Code | Name | Description
0x01 | Illegal function | The function code received in the query is not an allowable action for the server (or slave node). This may be because the function code is only applicable to newer devices, and was not implemented in the unit selected. It could also indicate that the server (or slave node) is in the wrong state to process a request of this type, for example because it is not configured and is being asked to return register values.
0x02 | Illegal data address | The data address received in the query is not an allowable address for the server. More specifically, the combination of reference number and transfer length is invalid. For a controller with 100 registers, the PDU addresses the first register as 0, and the last one as 99. If a request is submitted with a starting register address of 96 and a quantity of registers of 4, then this request will successfully operate (address-wise at least) on registers 96, 97, 98, 99. If a request is submitted with a starting register address of 96 and a quantity of registers of 5, then this request will fail with Exception Code 0x02 "Illegal Data Address" since it attempts to operate on registers 96, 97, 98, 99 and 100, and there is no register with address 100.
0x03 | Illegal data value | The value contained in the query data field is not an allowable value for the server (or slave). The value indicates a fault in the structure of the remainder of a complex request, such as an incorrectly implied length. It specifically does not mean that a data item submitted for storage in a register has a value outside the expectation of the application program since the Modbus protocol is unaware of the significance of any particular value of any particular register.
0x04 | Slave node failure | An error occurred while the server was attempting to perform the requested action.
0x06 | Slave device busy | The server cannot accept a Modbus request PDU. A client application determines whether and when to resend the request.

## Table 19
Code | Name |  | Description
0x80 | No permission |  | An operation is not allowed because of a permission authentication failure or permission expiration.
5.3.3 Reading Registers (0x03)
5.3.3.1 Frame Format of a Request from a Master Node
Data Field |  | Length (Byte) |  | Description
Function code |  | 1 |  | 0x03
Register start address |  | 2 |  | 0x0000–0xFFFF
Number of registers |  | 2 |  | 1–125
5.3.3.2 Frame Format of a Normal Response from a Slave Node
Data Field |  | Length (Byte) |  | Description
Function code |  | 1 |  | 0x03
Number of bytes |  | 1 |  | 2 x N
Register value |  | 2 x N |  | N/A
NOTE
N refers to the number of registers.
5.3.3.3 Frame Format of an Abnormal Response from a Slave Node
Data Field |  | Length (Byte) |  | Description
Function code |  | 1 |  | 0x83
Exception code |  | 1 |  | See Exception Code List.
5.3.3.4 Examples This section takes the Modbus-TCP communications frames as an example. The differences between Modbus-RTU and Modbus-TCP lie in the additional address field and the CRC. Pay attention to the differences when using the Modbus-RTU frames. This also works for the follow-up examples.
The master node sends a query request (register address: 32306/0X7E32) to the slave node (logical device ID: 00).

## Table 20
Description |  | Frame Data
MBAP header | Protocol identifier | 0
1
| Protocol type | 0
0
| Data length | 0
6
| Logical device ID | 0
Function code |  | 3
Data | Register address | 7E
32
| Number of registers | 0
2
Normal response from the slave node
Description |  | Frame Data
MBAP header | Protocol identifier | 0
1
| Protocol type | 0
0
| Data length | 0
7
| Logical device ID | 0
Function code |  | 3
Data | Number of bytes | 4
| Register data | 0
0
0
1

## Table 21
Abnormal response from the slave node
Description |  | Frame Data
MBAP header | Protocol identifier | 0
1
| Protocol type | 0
0
| Data length | 0
3
| Logical device ID | 0
Function code |  | 83
Data | Error code | 3
5.3.4 Writing a Single Register (0x06)
5.3.4.1 Frame Format of a Request from a Master Node
Data Field | Length (Byte) | Description
Function code | 1 | 0x06
Register address | 2 | 0x0000–0xFFFF
Register value | 2 | 0x0000–0xFFFF
5.3.4.2 Frame Format of a Normal Response from a Slave Node
Data Field | Length (Byte) | Description
Function code | 1 | 0x06
Register address | 2 | 0x0000–0xFFFF
Register value | 2 | 0x0000–0xFFFF
5.3.4.3 Frame Format of an Abnormal Response from a Slave Node
Data Field | Length (Byte) | Description
Function code | 1 | 0x86

## Table 22
Data Field | Length (Byte) | Description
Exception code | 1 | See Exception Code List.
5.3.4.4 Examples A master node sends a command (register address: 40200/0X9D08) to a slave node (address: 00).
Description |  | Frame Data
MBAP header | Protocol identifier | 0
1
| Protocol type | 0
0
| Data length | 0
6
| Logical device ID | 0
Function code |  | 6
Data | Register address | 9D
8
| Register data | 0
0
Normal response from the slave node
Description |  | Frame Data
MBAP header | Protocol identifier | 0
1
| Protocol type | 0
0
| Data length | 0
6
| Logical device ID | 0
Function code |  | 6
Description |  | Frame Data
Data | Register address | 9D
8
| Register data | 0
0

## Table 23
Abnormal response from the slave node
Description |  | Frame Data
MBAP header | Protocol identifier | 0
1
| Protocol type | 0
0
| Data length | 0
3
| Logical device ID | 0
Function code |  | 86
Data | Error code | 4
5.3.5 Writing Multiple Registers (0x10)
5.3.5.1 Frame Format of a Request from a Master Node
Data Field | Length (Byte) | Description
Function code | 1 | 0x10
Register start address | 2 | 0x0000–0xFFFF
Number of registers | 2 | 0x0000–0x007b
Number of bytes | 1 | 2 x N
Register value | 2 x N | Value
NOTE
N refers to the number of registers.
5.3.5.2 Frame Format of a Normal Response from a Slave Node

## Table 24
Data Field | Length (Byte) | Description
Function code | 1 | 0x10
Register address | 2 | 0x0000–0xFFFF
Number of registers | 2 | 0x0000–0x007b
5.3.5.3 Frame Format of an Abnormal Response from a Slave Node
Data Field | Length (Byte) | Description
Function code | 1 | 0x90
Exception code | 1 | See Exception Code List.
5.3.5.4 Examples The master node sets the register address 40118/0X9CB6 to 2 and the register address 40119/0X9CB7 to 50 for the slave node (address: 00). The request frame format is as follows.
Description |  | Frame Data
MBAP header | Protocol identifier | 0
1
| Protocol type | 0
0
| Data length | 0
0B
| Logical device ID | 0
Function code |  | 10
Data | Register address | 9C
B6
| Number of registers | 0
2
| Number of bytes | 4
| Register data | 0

## Table 25
Description |  | Frame Data
2
0
32
Normal response from the slave node
Description |  | Frame Data
MBAP header | Protocol identifier | 0
1
| Protocol type | 0
0
| Data length | 0
6
| Logical device ID | 0
Function code |  | 10
Data | Register address | 9C
B6
| Number of registers | 0
2
Abnormal response from the slave node
Description |  | Frame Data
MBAP header | Protocol identifier | 0
1
| Protocol type | 0
0
| Data length | 0
3
| Logical device ID | 0
Function code |  | 90
Description |  | Frame Data
Data | Error code | 4

## Table 26
5.3.6 Reading Device Identifiers (0x2B) This command code allows reading identifiers and added packets that are relevant to the physical and function description of the remote devices. Simulate the interface of the read device identifier as an address space. This address space consists of a set of addressable data elements. The data elements are objects to be read, and the object IDs determine these data elements. A data element consists of three objects: 1. Basic device identifier: All objects of this type are mandatory, such as the vendor name, product code, and revision version. 2. Normal device identifier: In addition to the basic data objects, the device provides additional and optional identifiers and data object description. Define all types of objects according to definitions in the standard, but the execution of this type of objects is optional. 3. Extended device identifier: In addition to the normal data objects, the device provides additional and optional identifiers and special data object description. All the data is related to the device.
Table 5-5 Reading device identifiers
Object ID | Object Name or Description | Type | Mandatory or Optional (M/O) | Type
0x00 | Manufacturer name | ASCII character string | M | Basic
0x01 | Product code | ASCII character string | M
0x02 | Main revision version | ASCII character string | M
0x03–0x7F | - | - | - | Normal
0x80–0xFF | - | - | - | Expansion

## Table 27
5.3.6.1 Command for Querying Device Identifiers
Table 5-6 Request frame format
Data Field |  |  | Length (Byte) |  |  |  | Description
Function code |  |  | 1 |  |  |  | 0x2B
MEI type |  |  | 1 |  |  |  | 0x0E
ReadDevId code |  |  | 1 |  |  |  | 1
Object ID |  |  | 1 |  |  |  | 0x00
Table 5-7 Frame format for a normal response
Data Field |  |  |  |  | Length (Byte) |  |  | Description
Function code |  |  |  |  | 1 |  |  | 0x2B
MEI type |  |  |  |  | 1 |  |  | 0x0E
ReadDevId code |  |  |  |  | 1 |  |  | 1
Consistency level |  |  |  |  | 1 |  |  | 1
More |  |  |  |  | 1 |  |  | -
Next object ID |  |  |  |  | 1 |  |  | -
Number of objects |  |  |  |  | 1 |  |  | -
Object list | First object |  |  | Objec t ID | 1 |  |  | 0x00
|  |  |  | Objec t length | 1 |  |  | N
|  |  |  | Objec t value | N |  |  | -
| ... |  |  | ... | ... |  |  | ...
Table 5-8 Object list
Object ID |  | Object Name or Description |  |  |  | Description |  | Type
0x00 |  | Manufacturer name |  |  |  | HUAWEI |  | Basic
0x01 |  | Product code |  |  |  | SUN2000
0x02 |  | Main revision version |  |  |  | ASCII character string, software version

## Table 28
Table 5-9 Frame format for an abnormal response
Data Field |  | Length (Byte) |  |  | Description
Function code |  | 1 |  |  | 0xAB
Exception code |  | 1 |  |  | See Exception Code List.
5.3.6.2 Command for Querying a Device List
Table 5-10 Request frame format
Data Field |  | Length (Byte) |  |  | Description
Function code |  | 1 |  |  | 0x2B
MEI type |  | 1 |  |  | 0x0E
ReadDevId code |  | 1 |  |  | 3
Object ID |  | 1 |  |  | 0x87
Table 5-11 Frame format for a normal response
Data Field |  |  |  | Length (Byte) |  | Description
Function code |  |  |  | 1 |  | 0x2B
MEI type |  |  |  | 1 |  | 0x0E
ReadDevId code |  |  |  | 1 |  | 3
Consistency level |  |  |  | 1 |  | 3
More |  |  |  | 1 |  | -
Next object ID |  |  |  | 1 |  | -
Number of objects |  |  |  | 1 |  | -
Object list | First object |  | Object ID | 1 |  | 0x87

## Table 29
Data Field |  |  |  |  | Length (Byte) | Description
|  |  | Object length |  | 1 | N
|  |  | Object value |  | N | -
| ... |  | ... |  | ... | ...
Table 5-12 Object list
Object ID |  | Object Name |  | Type |  | Description
0x80-0x86 |  | Reserved |  | - |  | Returns a null object with a length of 0.
0x87 |  | Number of devices |  | int |  | Returns the number of devices connected to the RS485 address.
0x88 |  | Description about the first device |  | ASCII character string See the device description definitions. |  | Returns only description about the first device if a NE allows only one device to be connected to each RS485 address.
0x8A |  | Description about the second device |  | - |  | -
- |  | - |  | - |  | -
0xFF |  | Description about the 120th device |  | - |  | -
5.3.6.3 Device Description Definition Each device description consists of all "attribute=value" character strings. "Attribute ID=%s;attribute ID=%s;... attribute ID=%s" For example: "1=SUN2000MA-XXKTL;2=V100R001C00SPC100;3=P1.0- D5.0;4=123232323;5=1;6=1.1"

## Table 30
Table 5-13 Attribute definition
Attribut e ID | Name |  | Type | Description
1 | Device model |  | ASCII character string | SUN2000
2 | Device software version |  | ASCII character string | -
3 | Port protocol version |  | ASCII character string | See the interface protocol version definitions.
4 | ESN |  | ASCII character string | -
5 | Device ID |  | int | 0, 1, 2, 3,... (assigned by NEs; 0 indicates the master device into which the Modbus card is inserted)
6 | Feature version |  | ASCII character string | -
Table 5-14 Frame format for an abnormal response
Data Field |  | Length (Byte) |  |  | Description
Function code |  | 1 |  |  | 0xAB
Exception code |  | 1 |  |  | See Exception Code List.
5.3.7 Huawei-defined Functions (0x41)
5.3.7.1 Uploading Files Uploading files means uploading them by stream data from a slave node to a master node. The following figure shows the file uploading process.

## Table 31
Figure 5-7 File uploading process
5.3.7.1.1 Starting the Upload Frame format of a request from a master node
Table 5-15 PDU data field of the request frame for starting upload (0x05)
PDU Data Field | Length (Byte) | Description
Function code | 1 | 0x41
Sub- function code | 1 | 0x05
Data length | 1 | 1 + N
File type | 1 | Unique ID of a file
Customi zed data | N | -

## Table 32
Table 5-16 PDU data field of the response frame for starting upload (0x05)
Data Field | Length (Byte) |  | Description
Function code | 1 |  | 0x41
Sub- function code | 1 |  | 0x05
Data length | 1 |  | 6 + N
File type | 1 |  | Unique ID of a file
File length | 4 |  | -
Data frame length | 1 |  | -
Customi zed data | N |  | -
Table 5-17 PDU data field in the abnormal response frame of the slave node
PDU Data Field |  | Length (Byte) |  | Description
Error code |  | 1 |  | 0xC1
Exception code |  | 1 |  | See Exception Code List.
NOTE
If the exception code is 0x06, resend the request after 10 seconds. A request can be resent for no more than six times. 5.3.7.1.2 Uploading Data
Table 5-18 Request frame for uploading data (0x06)
PDU Data Field |  | Length (Byte) |  | Description
Function code |  | 1 |  | 0x41
Sub-function code |  | 1 |  | 0x06

## Table 33
PDU Data Field | Length (Byte) | Description
Data length | 1 | 3
File type | 1 | Unique ID of a file
Frame No. | 2 | 0x0000–0xFFFF
Table 5-19 Response frame for uploading data (0x06)
PDU Data Field | Length (Byte) | Description
Function code | 1 | 0x41
Sub-function code | 1 | 0x06
Data length | 1 | 3 + N
File type | 1 | -
Frame No. | 2 | 0x0000–0xFFFF
Frame data | N | -
Table 5-20 Abnormal response frame for uploading data
PDU Data Field | Length (Byte) | Description
Error code | 1 | 0xC1
Exception code | 1 | See Exception Code List.
5.3.7.1.3 Completing the Data Upload
Table 5-21 Request frame for completing the data upload
PDU Data Field | Length (Byte) | Description
Function code | 1 | 0x41
Sub-function code | 1 | 0x0c
Data length | 1 | 1
File type | 1 | -

## Table 34
Table 5-22 Response frame for completing the data upload
PDU Data Field | Length (Byte) | Description
Function code | 1 | 0x41
Sub-function code | 1 | 0x0c
Data length | 1 | 3
File type | 1 | -
File CRC | 2 | -
Table 5-23 Abnormal response frame for completing the data upload
Data Field | Length (Byte) | Description
Error code | 1 | 0xC1
Exception code | 1 | See Exception Code List.
5.3.7.1.4 Timeout Processing
Table 5-24 Processing specifications of sub-process timeout
Name |  |  | Restraints
Response timeout period for starting an upload |  |  | 10s
Response timeout period for uploading data |  |  | 10s
Number of times of resending a data upload command |  |  | 6
Response timeout period for completing a data upload |  |  | 10s