## alarmo
147 | Alarm 1 |  | RO | Bitfield 16 | N/ A | 1 | 50000 | 1
148 | Alarm 2 |  | RO | Bitfield 16 | N/ A | 1 | 50001 | 1
149 | Alarm 3 |  | RO | Bitfield 16 | N/ A | 1 | 50002 | 1
150 | Alarm 4 |  | RO | Bitfield 16 | N/ A | 1 | 50003 | 1
151 | Alarm 5 |  | RO | Bitfield 16 | N/ A | 1 | 50004 | 1
152 | Alarm 6 |  | RO | Bitfield 16 | N/ A | 1 | 50005 | 1
153 | Alarm 7 |  | RO | Bitfield 16 | N/ A | 1 | 50006 | 1
154 | Alarm 8 |  | RO | Bitfield 16 | N/ A | 1 | 50007 | 1
155 | Alarm 9 |  | RO | Bitfield 16 | N/ A | 1 | 50008 | 1
156 | Alarm 10 |  | RO | Bitfield 16 | N/ A | 1 | 50009 | 1
157 | Alarm 11 |  | RO | Bitfield 16 | N/ A | 1 | 50010 | 1
158 | Alarm 12 |  | RO | Bitfield 16 | N/ A | 1 | 50011 | 1
159 | Alarm 13 |  | RO | Bitfield 16 | N/ A | 1 | 50012 | 1
160 | Alarm 14 |  | RO | Bitfield 16 | N/ A | 1 | 50013 | 1
161 | Alarm 15 |  | RO | Bitfield 16 | N/ A | 1 | 50014 | 1
162 | Alarm 16 |  | RO | Bitfield 16 | N/ A | 1 | 50015 | 1
163 | Alarm 17 |  | RO | Bitfield 16 | N/ A | 1 | 50016 | 1
1 | 50000 | 1 | Abnormal String 1 | 106 | 1
2 | 50000 | 2 | Abnormal String 2 | 107 | 1
3 | 50000 | 3 | Abnormal String 3 | 108 | 1
4 | 50000 | 4 | Abnormal String 4 | 109 | 1
5 | 50000 | 5 | Abnormal String 5 | 110 | 1
6 | 50000 | 6 | Abnormal String 6 | 111 | 1
7 | 50000 | 10 | Software Ver. Unmatch | 504 | 1
8 | 50000 | 12 | Upgrade Failed | 505 | 1
9 | 50000 | 13 | Flash Fault | 61440 | 1
10 | 50000 | 14 | License Expired | 506 | 1
11 | 50001 | 1 | Software Ver. Unmatch | 504 | 2
12 | 50001 | 2 | Software Ver. Unmatch | 504 | 3
13 | 50001 | 3 | System Fault | 400 | 1
14 | 50001 | 4 | System Fault | 400 | 27
15 | 50001 | 5 | Abnormal DC Circuit | 200 | 16
16 | 50001 | 6 | Abnormal Inv. Circuit | 202 | 20
17 | 50001 | 7 | Abn. Residual Curr. | 318 | 1
18 | 50001 | 8 | Overtemperature | 321 | 1
19 | 50001 | 10 | System Fault | 400 | 28
20 | 50001 | 11 | Fan Fault | 320 | 1
21 | 50001 | 12 | Abnormal SPI Comm. | 322 | 1
22 | 50001 | 14 | System Fault | 400 | 29
23 | 50002 | 0 | Low Insulation Resistance | 313 | 1
24 | 50002 | 1 | AFCI Self-Check Failure | 411 | 1
25 | 50002 | 2 | DC Arc Fault | 412 | 1
26 | 50002 | 3 | AFCI Self-Check Failure | 411 | 2
27 | 50002 | 4 | AFCI Self-Check Failure | 411 | 3
28 | 50002 | 5 | Abnormal Inv. Circuit | 202 | 21
29 | 50002 | 7 | System Fault | 400 | 30
30 | 50002 | 8 | System Fault | 400 | 31
31 | 50002 | 9 | String 3 Reversed | 122 | 1
32 | 50002 | 12 | DC Arc Fault | 412 | 2
33 | 50002 | 13 | DC Arc Fault | 412 | 3
34 | 50002 | 14 | DC Arc Fault | 412 | 4
35 | 50002 | 15 | System Fault | 400 | 23
36 | 50003 | 1 | String 1 Reversed | 120 | 1
37 | 50003 | 2 | String 2 Reversed | 121 | 1
38 | 50003 | 3 | Abnormal DC Circuit | 200 | 12
39 | 50003 | 6 | String 4 Reversed | 123 | 1
40 | 50003 | 7 | String 5 Reversed | 124 | 1
41 | 50003 | 8 | String 6 Reversed | 125 | 1
42 | 50003 | 9 | High DC Input Voltage | 103 | 1
43 | 50003 | 10 | High DC Input Voltage | 103 | 2
44 | 50003 | 11 | High DC Input Voltage | 103 | 3
45 | 50003 | 12 | High DC Input Voltage | 103 | 4
46 | 50003 | 15 | Abnormal DC Circuit | 200 | 15
47 | 50004 | 2 | String 1 Reversed | 120 | 2
48 | 50004 | 3 | String 2 Reversed | 121 | 2
49 | 50004 | 4 | String 7 Reversed | 126 | 1
50 | 50004 | 5 | String 7 Reversed | 126 | 2
51 | 50004 | 6 | String 8 Reversed | 127 | 1
52 | 50004 | 7 | String 8 Reversed | 127 | 2
53 | 50004 | 8 | Abnormal PV String Connection | 413 | 1
54 | 50004 | 9 | Abnormal PV String Connection | 413 | 2
55 | 50004 | 10 | Abnormal PV String Connection | 413 | 3
56 | 50004 | 11 | Abnormal PV String Connection | 413 | 4
57 | 50004 | 12 | String 3 Reversed | 122 | 2
58 | 50004 | 13 | String 4 Reversed | 123 | 2
59 | 50004 | 14 | String 5 Reversed | 124 | 2
60 | 50004 | 15 | String 6 Reversed | 125 | 2
61 | 50005 | 1 | Abnormal DC Circuit | 200 | 3
62 | 50005 | 2 | Abn. Auxiliary Power | 410 | 4
63 | 50005 | 4 | Abnormal DC Circuit | 200 | 10
64 | 50005 | 5 | Abnormal DC Circuit | 200 | 11
65 | 50005 | 6 | Abnormal DC Circuit | 200 | 30
66 | 50005 | 7 | BST Inductor Cable Connection Abnormal | 414 | 1
67 | 50005 | 8 | BST Inductor Cable Connection Abnormal | 414 | 2
68 | 50005 | 9 | BST Inductor Cable Connection Abnormal | 414 | 3
69 | 50005 | 10 | BST Inductor Cable Connection Abnormal | 414 | 4
70 | 50006 | 6 | System Fault | 400 | 3
71 | 50006 | 10 | Abnormal Inv. Circuit | 202 | 13
72 | 50006 | 12 | Abnormal Inv. Circuit | 202 | 14
73 | 50007 | 1 | Abnormal Inv. Circuit | 202 | 16
74 | 50007 | 5 | System Fault | 400 | 21
75 | 50008 | 0 | Abnormal Grid Voltage | 301 | 4
76 | 50008 | 3 | Abnormal Grid Voltage | 301 | 16
77 | 50008 | 6 | Abnormal Grid Frequency | 305 | 2
78 | 50008 | 7 | Abnormal Grid Frequency | 305 | 4
79 | 50008 | 8 | Abnormal Grid Voltage | 301 | 28
80 | 50008 | 9 | Abnormal Grid Voltage | 301 | 29
81 | 50008 | 10 | Abnormal Grounding | 326 | 1
82 | 50008 | 11 | Abnormal Grid Voltage | 301 | 26
83 | 50008 | 12 | Abnormal Grid Frequency | 305 | 5
84 | 50009 | 0 | Abnormal Grid Voltage | 301 | 31
85 | 50009 | 1 | Abnormal Grid Voltage | 301 | 32
86 | 50009 | 2 | Abnormal Grid Voltage | 301 | 33
87 | 50009 | 8 | Abnormal Grid Voltage | 301 | 19
88 | 50016 | 0 | Abnormal String 1 | 106 | 1
89 | 50016 | 1 | Abnormal String 2 | 107 | 1
90 | 50016 | 2 | Abnormal String 3 | 108 | 1
91 | 50016 | 3 | Abnormal String 4 | 109 | 1
92 | 50016 | 4 | Abnormal String 5 | 110 | 1
93 | 50016 | 5 | Abnormal String 6 | 111 | 1
94 | 50016 | 6 | Abnormal String 7 | 112 | 1
95 | 50016 | 7 | Abnormal String 8 | 113 | 1

## 3
No | Signal name | Type | Unit | Gain | Address | Number of regs | Scope
1 | Model ID | RO | U16 | N/ A | 1 | 32001 | 1
2 | Output mode | RO | U16 | N/ A | 1 | 32002 | 1
3 | SN | RO | STR | N/ A | 1 | 32003 | 10
4 | PN | RO | STR | N/ A | 1 | 32153 | 10
5 | System time | RO | EPOCH TIME | N/ A | 1 | 32200 | 2
6 | PV1 voltage | RO | I16 | V | 10 | 32262 | 1
7 | PV1 current | RO | I16 | A | 10 | 32263 | 1
8 | PV2 voltage | RO | I16 | V | 10 | 32264 | 1
9 | PV2 current | RO | I16 | A | 10 | 32265 | 1
10 | PV3 voltage | RO | I16 | V | 10 | 32266 | 1
11 | PV3 current | RO | I16 | A | 10 | 32267 | 1
12 | PV4 voltage | RO | I16 | V | 10 | 32268 | 1
13 | PV4 current | RO | I16 | A | 10 | 32269 | 1
14 | PV5 voltage | RO | I16 | V | 10 | 32270 | 1
15 | PV5 current | RO | I16 | A | 10 | 32271 | 1
16 | PV6 voltage | RO | I16 | V | 10 | 32272 | 1
17 | PV6 current | RO | I16 | A | 10 | 32273 | 1
18 | Line voltage between phases A and B | RO | U16 | V | 10 | 32274 | 1
19 | Line voltage between phases B and C | RO | U16 | V | 10 | 32275 | 1
20 | Line voltage between phases C and A | RO | U16 | V | 10 | 32276 | 1
21 | Phase A voltage | RO | U16 | V | 10 | 32277 | 1
22 | Phase B voltage | RO | U16 | V | 10 | 32278 | 1
23 | Phase C voltage | RO | U16 | V | 10 | 32279 | 1
24 | Phase A current | RO | U16 | A | 10 | 32280 | 1
25 | Phase B current | RO | U16 | A | 10 | 32281 | 1
26 | Phase C current | RO | U16 | A | 10 | 32282 | 1
27 | Grid frequency | RO | U16 | Hz | 100 | 32283 | 1
28 | Power factor | RO | I16 | N/ A | 1000 | 32284 | 1
29 | Inverter efficiency | RO | U16 | % | 100 | 32285 | 1
30 | Internal temperature | RO | I16 | °C | 10 | 32286 | 1
31 | Device status | RO | U16 | N/ A | 1 | 32287 | 1
32 | Peak active power of current day | RO | I32 | kW | 1000 | 32288 | 2
33 | Active power | RO | I32 | kW | 1000 | 32290 | 2
34 | Reactive power | RO | I32 | kVa r | 1000 | 32292 | 2
35 | Input power | RO | U32 | kW | 1000 | 32294 | 2
36 | Current energy yield collection time | RO | EPOCH TIME | N/ A | 1 | 32296 | 2
37 | Energy yield in current hour | RO | U32 | kW h | 100 | 32298 | 2
38 | Daily energy yield | RO | U32 | kW h | 100 | 32300 | 2
39 | Monthly energy yield | RO | U32 | kW h | 100 | 32302 | 2
40 | Annual energy yield | RO | U32 | kW h | 100 | 32304 | 2
41 | Accumulated energy yield | RO | U32 | kW h | 100 | 32306 | 2
42 | PV7 voltage | RO | I16 | V | 10 | 32314 | 1
43 | PV7 current | RO | I16 | A | 10 | 32315 | 1
44 | PV8 voltage | RO | I16 | V | 10 | 32316 | 1
45 | PV8 current | RO | I16 | A | 10 | 32317 | 1
46 | State 1 | RO | Bitfield 16 | N/ A | 1 | 32319 | 1
47 | State 2 | RO | Bitfield 16 | N/ A | 1 | 32320 | 1
48 | State 3 | RO | Bitfield 16 | N/ A | 1 | 32321 | 1
49 | State 4 | RO | Bitfield 16 | N/ A | 1 | 32322 | 1
50 | Insulation resistance | RO | U16 | M Ω | 1000 | 32323 | 1
51 | Startup time | RO | EPOCH TIME | s | 1 | 32325 | 2
52 | Shutdown time | RO | EPOCH TIME | s | 1 | 32327 | 2
53 | Energy yield collection time for previous hour | RO | EPOCH TIME | N/ A | 1 | 32343 | 2
54 | Energy yield in previous hour | RO | U32 | kW h | 100 | 32345 | 2
55 | Energy yield collection time for previous day | RO | EPOCH TIME | N/ A | 1 | 32347 | 2
56 | Energy yield on previous day | RO | U32 | kW h | 100 | 32349 | 2
57 | Energy yield collection time for previous month | RO | EPOCH TIME | N/ A | 1 | 32351 | 2
58 | Energy yield in previous month | RO | U32 | kW h | 100 | 32353 | 2
59 | Energy yield collection time for previous year | RO | EPOCH TIME | N/ A | 1 | 32355 | 2
60 | Energy yield in previous year | RO | U32 | kW h | 100 | 32357 | 2
61 | [Active] Adjustment mode | RO | U16 | N/ A | 1 | 32402 | 1
62 | [Active] Adjustment value | RO | U32 | N/ A |  | 32403 | 2
63 | [Active] Adjustment command | RO | U16 | N/ A | 1 | 32405 | 1
64 | [Reactive] Adjustment mode | RO | U16 | N/ A | 1 | 32406 | 1
65 | [Reactive] Adjustment value | RO | U32 | N/ A |  | 32407 | 2
66 | [Reactive] Adjustment command | RO | U16 | N/ A | 1 | 32409 | 1
67 | MPPT1 total input power | RO | U32 | kW | 1000 | 33022 | 2
68 | MPPT2 total input power | RO | U32 | kW | 1000 | 33024 | 2
69 | MPPT3 total input power | RO | U32 | kW | 1000 | 33026 | 2
70 | MPPT4 total input power | RO | U32 | kW | 1000 | 33070 | 2
71 | System time | RW | EPOCH TIME | N/ A | 1 | 40000 | 2
72 | [Power grid scheduling] Reactive power compensation mode | RW | U16 | N/ A | 1 | 40117 | 1
73 | [Power grid scheduling] Active power control mode | RW | U16 | N/ A | 1 | 40118 | 1
74 | [Power grid scheduling] Active power percentage derating (1%) | RW | U16 | % | 1 | 40119 | 1
75 | [Power grid scheduling] Fixed active power derated | RW | U16 | kW | 10 | 40120 | 1
76 | [Power grid scheduling] Active power change gradient | RW | U16 | %/s | 10 | 40121 | 1
77 | [Power grid scheduling] Reactive power compensation (PF) | RW | I16 | N/ A | 1000 | 40122 | 1
78 | [Power grid scheduling] Reactive power compensation (Q/S) | RW | I16 | N/ A | 1000 | 40123 | 1
79 | [Power grid scheduling] Reactive power adjustment time | RW | U16 | s | 1 | 40124 | 1
80 | [Power grid scheduling] Active power percentage derating (0.1%) | RW | U16 | % | 10 | 40125 | 1
81 | [Power grid scheduling] cosφ-P/Pn characteristic curve | RW | BYTES | N/ A | 1 | 40133 | 21
82 | [Power grid scheduling] Q- U characteristic curve | RW | BYTES | N/ A | 1 | 40154 | 21
83 | [Power grid scheduling] Q- U power percentage to exit scheduling | RW | U16 | % | 1 | 40198 | 1
84 | Startup | WO | U16 | N/ A | 1 | 40200 | 1
85 | Shutdown | WO | U16 | N/ A | 1 | 40201 | 1
86 | [Power grid scheduling] Active power percentage derating command (0.1%) | WO | U16 | % | 10 | 40232 | 1
87 | [Power grid scheduling] Fixed active power derating command (1%) | WO | U16 | % | 1 | 40234 | 1
88 | [Power grid scheduling] Fixed active power derating command | WO | U16 | kW | 10 | 40235 | 1
89 | [Power grid scheduling] Reactive power compensation command (Q/S) | WO | I16 | N/ A | 1000 | 40236 | 1
90 | [Power grid scheduling] Reactive power compensation command (PF) | WO | I16 | N/ A | 1000 | 40237 | 1
91 | Level-1 OV protection time | RW | U32 | ms | 1 | 42045 | 2
92 | Level-2 OV protection time | RW | U32 | ms | 1 | 42047 | 2
93 | Level-1 UV protection time | RW | U32 | ms | 1 | 42049 | 2
94 | Level-2 UV protection time | RW | U32 | ms | 1 | 42051 | 2
95 | Level-1 OF protection time | RW | U32 | ms | 1 | 42053 | 2
96 | Level-2 OF protection time | RW | U32 | ms | 1 | 42055 | 2
97 | Level-1 UF protection time | RW | U32 | ms | 1 | 42057 | 2
98 | Level-2 UF protection time | RW | U32 | ms | 1 | 42059 | 2
99 | 10-minute OV protection time | RW | U32 | ms | 1 | 42061 | 2
100 | Level-1 OV protection | RW | U16 | V | 10 | 42063 | 1
101 | Level-2 OV protection | RW | U16 | V | 10 | 42064 | 1
102 | Level-1 UV protection | RW | U16 | V | 10 | 42065 | 1
103 | Level-2 UV protection | RW | U16 | V | 10 | 42066 | 1
104 | Level-1 OF protection | RW | U16 | Hz | 100 | 42067 | 1
105 | Level-2 OF protection | RW | U16 | Hz | 100 | 42068 | 1
106 | Level-1 UF protection | RW | U16 | Hz | 100 | 42069 | 1
107 | Level-2 UF protection | RW | U16 | Hz | 100 | 42070 | 1
108 | 10 minute OV protection | RW | U16 | V | 10 | 42071 | 1
109 | Grid code | RW | U16 | N/ A | 1 | 42072 | 1
110 | Insulation resistance protection | RW | U16 | M Ω | 1000 | 42074 | 1
111 | Unbalance voltage protection | RW | U16 | % | 10 | 42075 | 1
112 | Soft start time after grid failure | RW | U16 | s | 1 | 42083 | 1
113 | LVRT | RW | U16 | N/ A | 1 | 42084 | 1
114 | Soft start time | RW | U16 | s | 1 | 42085 | 1
115 | Grid connection duration after grid recovery | RW | U16 | s | 1 | 42086 | 1
116 | Active islanding protection | RW | U16 | N/ A | 1 | 42087 | 1
117 | LVRT reactive power compensation power factor | RW | U16 | N/ A | 10 | 42089 | 1
118 | Reactive power compensation (cosφ-P) trigger voltage | RW | U16 | % | 1 | 42090 | 1
119 | Reactive power compensation (cosφ-P) exit voltage | RW | U16 | % | 1 | 42091 | 1
120 | Trigger frequency of overfrequency derating | RW | U16 | Hz | 100 | 42092 | 1
121 | Quit frequency of overfrequency derating | RW | U16 | Hz | 100 | 42093 | 1
122 | Power recovery gradient of overfrequency derating | RW | U16 | %/ mi n | 1 | 42094 | 1
123 | Q-U characteristic curve mode | RW | U16 | N/ A | 1 | 42095 | 1
124 | Q-U scheduling trigger power percent | RW | U16 | % | 1 | 42096 | 1
125 | MPPT multi- peak scanning | RW | U16 | N/ A | 1 | 42097 | 1
126 | MPPT scanning interval | RW | U16 | mi n | 1 | 42101 | 1
127 | AFCI | RW | U16 |  | 1 | 42125 | 1
128 | Level-3 OV protection | RW | U16 | V | 10 | 42151 | 1
129 | Level-3 OV protection time | RW | U32 | ms | 1 | 42152 | 2
130 | Level-4 OV protection | RW | U16 | V | 10 | 42154 | 1
131 | Level-4 OV protection time | RW | U32 | ms | 1 | 42155 | 2
132 | Level-3 UV protection | RW | U16 | V | 10 | 42157 | 1
133 | Level-3 UV protection time | RW | U32 | ms | 1 | 42158 | 2
134 | Level-4 UV protection | RW | U16 | V | 10 | 42160 | 1
135 | Level-4 UV protection time | RW | U32 | ms | 1 | 42161 | 2
136 | Shutdown at 0% power limit | RW | U16 | N/ A | 1 | 42174 | 1
137 | System time: year | RW | U16 | N/ A | 1 | 42300 | 1
138 | System time: month | RW | U16 | N/ A | 1 | 42301 | 1
139 | System time: day | RW | U16 | N/ A | 1 | 42302 | 1
140 | System time: hour | RW | U16 | N/ A | 1 | 42303 | 1
141 | System time: minute | RW | U16 | N/ A | 1 | 42304 | 1
142 | System time: second | RW | U16 | N/ A | 1 | 42305 | 1
143 | [Power grid scheduling] Active power percentage derating | RW | U16 | % | 1 | 42320 | 1
144 | [Power grid scheduling] Power factor | RW | I16 | N/ A | 1000 | 42321 | 1
145 | Remote power scheduling | RW | U16 | N/ A | 1 | 42333 | 1
146 | AFCI self check | WO | U16 | N/ A | 1 | 42731 | 1
147 | Alarm 1 | RO | Bitfield 16 | N/ A | 1 | 50000 | 1
148 | Alarm 2 | RO | Bitfield 16 | N/ A | 1 | 50001 | 1
149 | Alarm 3 | RO | Bitfield 16 | N/ A | 1 | 50002 | 1
150 | Alarm 4 | RO | Bitfield 16 | N/ A | 1 | 50003 | 1
151 | Alarm 5 | RO | Bitfield 16 | N/ A | 1 | 50004 | 1
152 | Alarm 6 | RO | Bitfield 16 | N/ A | 1 | 50005 | 1
153 | Alarm 7 | RO | Bitfield 16 | N/ A | 1 | 50006 | 1
154 | Alarm 8 | RO | Bitfield 16 | N/ A | 1 | 50007 | 1
155 | Alarm 9 | RO | Bitfield 16 | N/ A | 1 | 50008 | 1
156 | Alarm 10 | RO | Bitfield 16 | N/ A | 1 | 50009 | 1
157 | Alarm 11 | RO | Bitfield 16 | N/ A | 1 | 50010 | 1
158 | Alarm 12 | RO | Bitfield 16 | N/ A | 1 | 50011 | 1
159 | Alarm 13 | RO | Bitfield 16 | N/ A | 1 | 50012 | 1
160 | Alarm 14 | RO | Bitfield 16 | N/ A | 1 | 50013 | 1
161 | Alarm 15 | RO | Bitfield 16 | N/ A | 1 | 50014 | 1
162 | Alarm 16 | RO | Bitfield 16 | N/ A | 1 | 50015 | 1
163 | Alarm 17 | RO | Bitfield 16 | N/ A | 1 | 50016 | 1
1 | Active power control mode | RW | U16 |  | 1 | 40118 | 1 | Stores data but does not support high- frequency write operations.
2 | Active power percentage derating (1%) | RW | U16 | % | 1 | 40119 | 1
3 | Fixed active power derating | RW | U16 | kW | 10 | 40120 | 1
4 | Active power change gradient | RW | U16 | %/s | 10 | 40121 | 1
5 | Active power percentage derating (0.1%) | RW | U16 | % | 10 | 40125 | 1
6 | Active power percentage derating command (0.1%) | WO | U16 | % | 10 | 40232 | 1 | Supports high- frequency write operations but does not store data.
7 | Active power percentage derating command (1%) | WO | U16 | % | 1 | 40234 | 1
8 | Fixed active power derating command | WO | U16 | kW | 10 | 40235 | 1
1 | Reactive power compensation | RW | U16 |  | 1 | 40117 | 1 | Stores data but does not support high-
2 | Reactive power compensation (PF) | RW | I16 |  | 1000 | 40122 | 1 | frequency write operations.
3 | Reactive power compensation (Q/S) | RW | I16 |  | 1000 | 40123 | 1
4 | Reactive power adjustment time | RW | U16 | s | 1 | 40124 | 1
5 | Reactive power compensation command (Q/S) | WO | I16 |  | 1000 | 40236 | 1 | Supports high- frequency write operations but does not store data.
6 | Reactive power compensation command (PF) | WO | I16 |  | 1000 | 40237 | 1