## Table 1
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
5 | SUN2000 V100R001C81 | 8.8 | 5.28 | 8.8 | 8 | 4
4 | SUN2000 V100R001C81 | 11 | 6.6 | 11 | 10 | 4
3 | SUN2000 V100R001C81 | 13.2 | 7.92 | 13.2 | 12 | 4
2 | SUN2000 V100R001C81 | 16.5 | 9.9 | 16.5 | 15 | 6
1 | SUN2000 V100R001C81 | 18.7 | 11.22 | 18.7 | 17 | 6
0 | SUN2000 V100R001C81 | 22 | 13.2 | 22 | 20 | 6
25 | SUN2000 V200R001C02 | 22.2 | 14.64 | 24.4 | 22.2 | 6
17 | SUN2000 V100R001C81 | 23 | 13.8 | 23 | 23 | 6
16 | SUN2000 V100R001C81 | 24.5 | 14.7 | 24.5 | 24.5 | 6
32 | SUN2000 V200R002C00 | 24.7 | 15 | 25 | 24.7 | 8
21 | SUN2000 V200R001C02 | 25 | 16.5 | 27.5 | 25 | 6
18 | SUN2000 V100R001C81 | 27.5 | 16.5 | 27.5 | 27.5 | 6
60 | SUN2000 V200R002C00 | 29.9 | 17.94 | 29.9 | 29.9 | 8
22 | SUN2000 V200R001C02 | 30 | 19.8 | 33 | 30 | 6
23 | SUN2000 V200R001C90 | 30 | 19.8 | 33 | 30 | 6
19 | SUN2000 V200R001C90 | 33 | 19.8 | 33 | 30 | 6
43 | SUN2000 V200R002C00 | 33 | 19.8 | 33 | 30 | 8
44 | SUN2000 V200R001C90 | 30 | 19.8 | 33 | 30 | 6
28 | SUN2000 V200R002C00 | 33.3 | 22.8 | 38 | 33.3 | 8
36 | SUN2000 V200R002C20 | 36.6 | 21.96 | 36.6 | 33.3 | 8
20 | SUN2000 V200R001C90 | 40 | 24 | 40 | 36 | 6
27 | SUN2000 V200R002C00 | 40 | 24 | 40 | 36 | 8
37 | SUN2000 V200R002C20 | 40 | 24 | 40 | 36 | 8
29 | SUN2000 V200R002C00 | 40 | 27.6 | 46 | 40 | 8
35 | SUN2000 V200R002C20 | 44 | 26.4 | 44 | 40 | 8
26 | SUN2000 V200R002C00 | 47 | 28.2 | 47 | 42 | 8
31 | SUN2000 V200R002C00 | 52.5 | 31.5 | 52.5 | 43 | 8
34 | SUN2000HA V100R001C00 | 50 | 30 | 50 | 45 | 8
30 | SUN2000 V200R002C00 | 50.5 | 30.3 | 50.5 | 46 | 8
24 | SUN2000 V200R002C00 | 52.5 | 31.5 | 52.5 | 47.5 | 8
38 | SUN2000HA V100R001C00 | 60 | 36 | 60 | 55 | 8
39 | SUN2000HA V100R001C00 | 66 | 39.6 | 66 | 55 | 8
40 | SUN2000HA V100R001C00 | 66 | 39.6 | 66 | 55 | 8
33 | SUN2000HA V100R001C00 | 66 | 39.6 | 66 | 60 | 8
41 | SUN2000HA V100R001C00 | 66 | 39.6 | 66 | 60 | 8

## Table 3
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 | Model ID |  | RO | U16 | N/ A | 1 | 3200 1 | 1
2 | Output mode |  | RO | U16 | N/ A | 1 | 3200 2 | 1
3 | SN |  | RO | STR | N/ A | 1 | 3200 3 | 10
4 | PN |  | RO | STR | N/ A | 1 | 3215 3 | 10
5 | System time |  | RO | EPOCH TIME | N/ A | 1 | 3220 0 | 2
6 | PV1 voltage |  | RO | I16 | V | 10 | 3226 2 | 1
7 | PV1 current |  | RO | I16 | A | 10 | 3226 3 | 1
8 | PV2 voltage |  | RO | I16 | V | 10 | 3226 4 | 1
9 | PV2 current |  | RO | I16 | A | 10 | 3226 5 | 1
10 | PV3 voltage |  | RO | I16 | V | 10 | 3226 6 | 1
11 | PV3 current |  | RO | I16 | A | 10 | 3226 7 | 1
12 | PV4 voltage |  | RO | I16 | V | 10 | 3226 8 | 1
13 | PV4 current |  | RO | I16 | A | 10 | 3226 9 | 1
14 | PV5 voltage |  | RO | I16 | V | 10 | 3227 0 | 1
15 | PV5 current |  | RO | I16 | A | 10 | 3227 1 | 1
16 | PV6 voltage |  | RO | I16 | V | 10 | 3227 2 | 1
17 | PV6 current |  | RO | I16 | A | 10 | 3227 3 | 1
18 | Line voltage between phases A and B |  | RO | U16 | V | 10 | 3227 4 | 1
19 | Line voltage between phases B and C |  | RO | U16 | V | 10 | 3227 5 | 1
20 | Line voltage between phases C and A |  | RO | U16 | V | 10 | 3227 6 | 1
21 | Phase A voltage |  | RO | U16 | V | 10 | 3227 7 | 1
22 | Phase B voltage |  | RO | U16 | V | 10 | 3227 8 | 1
23 | Phase C voltage |  | RO | U16 | V | 10 | 3227 9 | 1
24 | Phase A current |  | RO | U16 | A | 10 | 3228 0 | 1
25 | Phase B current |  | RO | U16 | A | 10 | 3228 1 | 1
26 | Phase C current |  | RO | U16 | A | 10 | 3228 2 | 1
27 | Grid frequency |  | RO | U16 | Hz | 100 | 3228 3 | 1
28 | Power factor |  | RO | I16 | N/ A | 1000 | 3228 4 | 1
29 | Inverter efficiency |  | RO | U16 | % | 100 | 3228 5 | 1
30 | Internal temperature |  | RO | I16 | °C | 10 | 3228 6 | 1
31 | Device status |  | RO | U16 | N/ A | 1 | 3228 7 | 1
32 | Peak active power of current day |  | RO | I32 | kW | 1000 | 3228 8 | 2
33 | Active power |  | RO | I32 | kW | 1000 | 3229 0 | 2
34 | Reactive power |  | RO | I32 | kVa r | 1000 | 3229 2 | 2
35 | Input power |  | RO | U32 | kW | 1000 | 3229 4 | 2
36 | Current energy yield collection time |  | RO | EPOCH TIME | N/ A | 1 | 3229 6 | 2
37 | Energy yield in current hour |  | RO | U32 | kW h | 100 | 3229 8 | 2
38 | Daily energy yield |  | RO | U32 | kW h | 100 | 3230 0 | 2
39 | Monthly energy yield |  | RO | U32 | kW h | 100 | 3230 2 | 2
40 | Annual energy yield |  | RO | U32 | kW h | 100 | 3230 4 | 2
41 | Accumulated energy yield |  | RO | U32 | kW h | 100 | 3230 6 | 2
42 | PV7 voltage |  | RO | I16 | V | 10 | 3231 4 | 1
43 | PV7 current |  | RO | I16 | A | 10 | 3231 5 | 1
44 | PV8 voltage |  | RO | I16 | V | 10 | 3231 6 | 1
45 | PV8 current |  | RO | I16 | A | 10 | 3231 7 | 1
46 | State 1 |  | RO | Bitfield 16 | N/ A | 1 | 3231 9 | 1
47 | State 2 |  | RO | Bitfield 16 | N/ A | 1 | 3232 0 | 1
48 | State 3 |  | RO | Bitfield 16 | N/ A | 1 | 3232 1 | 1
49 | State 4 |  | RO | Bitfield 16 | N/ A | 1 | 3232 2 | 1
50 | Insulation resistance |  | RO | U16 | M Ω | 1000 | 3232 3 | 1
51 | Startup time |  | RO | EPOCH TIME | s | 1 | 3232 5 | 2
52 | Shutdown time |  | RO | EPOCH TIME | s | 1 | 3232 7 | 2
53 | Energy yield collection time for previous hour |  | RO | EPOCH TIME | N/ A | 1 | 3234 3 | 2
54 | Energy yield in previous hour |  | RO | U32 | kW h | 100 | 3234 5 | 2
55 | Energy yield collection time for previous day |  | RO | EPOCH TIME | N/ A | 1 | 3234 7 | 2
56 | Energy yield on previous day |  | RO | U32 | kW h | 100 | 3234 9 | 2
57 | Energy yield collection time for previous month |  | RO | EPOCH TIME | N/ A | 1 | 3235 1 | 2
58 | Energy yield in previous month |  | RO | U32 | kW h | 100 | 3235 3 | 2
59 | Energy yield collection time for previous year |  | RO | EPOCH TIME | N/ A | 1 | 3235 5 | 2
60 | Energy yield in previous year |  | RO | U32 | kW h | 100 | 3235 7 | 2
61 | [Active] Adjustment mode |  | RO | U16 | N/ A | 1 | 3240 2 | 1
62 | [Active] Adjustment value |  | RO | U32 | N/ A |  | 3240 3 | 2
63 | [Active] Adjustment command |  | RO | U16 | N/ A | 1 | 3240 5 | 1
64 | [Reactive] Adjustment mode |  | RO | U16 | N/ A | 1 | 3240 6 | 1
65 | [Reactive] Adjustment value |  | RO | U32 | N/ A |  | 3240 7 | 2
66 | [Reactive] Adjustment command |  | RO | U16 | N/ A | 1 | 3240 9 | 1
67 | MPPT1 total input power |  | RO | U32 | kW | 1000 | 3302 2 | 2
68 | MPPT2 total input power |  | RO | U32 | kW | 1000 | 3302 4 | 2
69 | MPPT3 total input power |  | RO | U32 | kW | 1000 | 3302 6 | 2
70 | MPPT4 total input power |  | RO | U32 | kW | 1000 | 3307 0 | 2
71 | System time |  | RW | EPOCH TIME | N/ A | 1 | 4000 0 | 2
72 | [Power grid scheduling] Reactive power compensation mode |  | RW | U16 | N/ A | 1 | 4011 7 | 1
73 | [Power grid scheduling] Active power control mode |  | RW | U16 | N/ A | 1 | 4011 8 | 1
74 | [Power grid scheduling] Active power percentage derating (1%) |  | RW | U16 | % | 1 | 4011 9 | 1
75 | [Power grid scheduling] Fixed active power derated |  | RW | U16 | kW | 10 | 4012 0 | 1
76 | [Power grid scheduling] Active power change gradient |  | RW | U16 | %/s | 10 | 4012 1 | 1
77 | [Power grid scheduling] Reactive power compensation (PF) |  | RW | I16 | N/ A | 1000 | 4012 2 | 1
78 | [Power grid scheduling] Reactive power compensation (Q/S) |  | RW | I16 | N/ A | 1000 | 4012 3 | 1
79 | [Power grid scheduling] Reactive power adjustment time |  | RW | U16 | s | 1 | 4012 4 | 1
80 | [Power grid scheduling] Active power percentage derating (0.1%) |  | RW | U16 | % | 10 | 4012 5 | 1
81 | [Power grid scheduling] cosφ-P/Pn characteristic curve |  | RW | BYTES | N/ A | 1 | 4013 3 | 21
82 | [Power grid scheduling] Q- U characteristic curve |  | RW | BYTES | N/ A | 1 | 4015 4 | 21
83 | [Power grid scheduling] Q- U power percentage to exit scheduling |  | RW | U16 | % | 1 | 4019 8 | 1
84 | Startup |  | WO | U16 | N/ A | 1 | 4020 0 | 1
85 | Shutdown |  | WO | U16 | N/ A | 1 | 4020 1 | 1
86 | [Power grid scheduling] Active power percentage derating command (0.1%) |  | WO | U16 | % | 10 | 4023 2 | 1
87 | [Power grid scheduling] Fixed active power derating command (1%) |  | WO | U16 | % | 1 | 4023 4 | 1
88 | [Power grid scheduling] Fixed active power derating command |  | WO | U16 | kW | 10 | 4023 5 | 1
89 | [Power grid scheduling] Reactive power compensation command (Q/S) |  | WO | I16 | N/ A | 1000 | 4023 6 | 1
90 | [Power grid scheduling] Reactive power compensation command (PF) |  | WO | I16 | N/ A | 1000 | 4023 7 | 1
91 | Level-1 OV protection time |  | RW | U32 | ms | 1 | 4204 5 | 2
92 | Level-2 OV protection time |  | RW | U32 | ms | 1 | 4204 7 | 2
93 | Level-1 UV protection time |  | RW | U32 | ms | 1 | 4204 9 | 2
94 | Level-2 UV protection time |  | RW | U32 | ms | 1 | 4205 1 | 2
95 | Level-1 OF protection time |  | RW | U32 | ms | 1 | 4205 3 | 2
96 | Level-2 OF protection time |  | RW | U32 | ms | 1 | 4205 5 | 2
97 | Level-1 UF protection time |  | RW | U32 | ms | 1 | 4205 7 | 2
98 | Level-2 UF protection time |  | RW | U32 | ms | 1 | 4205 9 | 2
99 | 10-minute OV protection time |  | RW | U32 | ms | 1 | 4206 1 | 2
100 | Level-1 OV protection |  | RW | U16 | V | 10 | 4206 3 | 1
101 | Level-2 OV protection |  | RW | U16 | V | 10 | 4206 4 | 1
102 | Level-1 UV protection |  | RW | U16 | V | 10 | 4206 5 | 1
103 | Level-2 UV protection |  | RW | U16 | V | 10 | 4206 6 | 1
104 | Level-1 OF protection |  | RW | U16 | Hz | 100 | 4206 7 | 1
105 | Level-2 OF protection |  | RW | U16 | Hz | 100 | 4206 8 | 1
106 | Level-1 UF protection |  | RW | U16 | Hz | 100 | 4206 9 | 1
107 | Level-2 UF protection |  | RW | U16 | Hz | 100 | 4207 0 | 1
108 | 10 minute OV protection |  | RW | U16 | V | 10 | 4207 1 | 1
109 | Grid code |  | RW | U16 | N/ A | 1 | 4207 2 | 1
110 | Insulation resistance protection |  | RW | U16 | M Ω | 1000 | 4207 4 | 1
111 | Unbalance voltage protection |  | RW | U16 | % | 10 | 4207 5 | 1
112 | Soft start time after grid failure |  | RW | U16 | s | 1 | 4208 3 | 1
113 | LVRT |  | RW | U16 | N/ A | 1 | 4208 4 | 1
114 | Soft start time |  | RW | U16 | s | 1 | 4208 5 | 1
115 | Grid connection duration after grid recovery |  | RW | U16 | s | 1 | 4208 6 | 1
116 | Active islanding protection |  | RW | U16 | N/ A | 1 | 4208 7 | 1
117 | LVRT reactive power compensation power factor |  | RW | U16 | N/ A | 10 | 4208 9 | 1
118 | Reactive power compensation (cosφ-P) trigger voltage |  | RW | U16 | % | 1 | 4209 0 | 1
119 | Reactive power compensation (cosφ-P) exit voltage |  | RW | U16 | % | 1 | 4209 1 | 1
120 | Trigger frequency of overfrequency derating |  | RW | U16 | Hz | 100 | 4209 2 | 1
121 | Quit frequency of overfrequency derating |  | RW | U16 | Hz | 100 | 4209 3 | 1
122 | Power recovery gradient of overfrequency derating |  | RW | U16 | %/ mi n | 1 | 4209 4 | 1
123 | Q-U characteristic curve mode |  | RW | U16 | N/ A | 1 | 4209 5 | 1
124 | Q-U scheduling trigger power percent |  | RW | U16 | % | 1 | 4209 6 | 1
125 | MPPT multi- peak scanning |  | RW | U16 | N/ A | 1 | 4209 7 | 1
126 | MPPT scanning interval |  | RW | U16 | mi n | 1 | 4210 1 | 1
127 | AFCI |  | RW | U16 |  | 1 | 4212 5 | 1
128 | Level-3 OV protection |  | RW | U16 | V | 10 | 4215 1 | 1
129 | Level-3 OV protection time |  | RW | U32 | ms | 1 | 4215 2 | 2
130 | Level-4 OV protection |  | RW | U16 | V | 10 | 4215 4 | 1
131 | Level-4 OV protection time |  | RW | U32 | ms | 1 | 4215 5 | 2
132 | Level-3 UV protection |  | RW | U16 | V | 10 | 4215 7 | 1
133 | Level-3 UV protection time |  | RW | U32 | ms | 1 | 4215 8 | 2
134 | Level-4 UV protection |  | RW | U16 | V | 10 | 4216 0 | 1
135 | Level-4 UV protection time |  | RW | U32 | ms | 1 | 4216 1 | 2
136 | Shutdown at 0% power limit |  | RW | U16 | N/ A | 1 | 4217 4 | 1
137 | System time: year |  | RW | U16 | N/ A | 1 | 4230 0 | 1
138 | System time: month |  | RW | U16 | N/ A | 1 | 4230 1 | 1
139 | System time: day |  | RW | U16 | N/ A | 1 | 4230 2 | 1
140 | System time: hour |  | RW | U16 | N/ A | 1 | 4230 3 | 1
141 | System time: minute |  | RW | U16 | N/ A | 1 | 4230 4 | 1
142 | System time: second |  | RW | U16 | N/ A | 1 | 4230 5 | 1
143 | [Power grid scheduling] Active power percentage derating |  | RW | U16 | % | 1 | 4232 0 | 1
144 | [Power grid scheduling] Power factor |  | RW | I16 | N/ A | 1000 | 4232 1 | 1
145 | Remote power scheduling |  | RW | U16 | N/ A | 1 | 4233 3 | 1
146 | AFCI self check |  | WO | U16 | N/ A | 1 | 4273 1 | 1
147 | Alarm 1 |  | RO | Bitfield 16 | N/ A | 1 | 5000 0 | 1
148 | Alarm 2 |  | RO | Bitfield 16 | N/ A | 1 | 5000 1 | 1
149 | Alarm 3 |  | RO | Bitfield 16 | N/ A | 1 | 5000 2 | 1
150 | Alarm 4 |  | RO | Bitfield 16 | N/ A | 1 | 5000 3 | 1
151 | Alarm 5 |  | RO | Bitfield 16 | N/ A | 1 | 5000 4 | 1
152 | Alarm 6 |  | RO | Bitfield 16 | N/ A | 1 | 5000 5 | 1
153 | Alarm 7 |  | RO | Bitfield 16 | N/ A | 1 | 5000 6 | 1
154 | Alarm 8 |  | RO | Bitfield 16 | N/ A | 1 | 5000 7 | 1
155 | Alarm 9 |  | RO | Bitfield 16 | N/ A | 1 | 5000 8 | 1
156 | Alarm 10 |  | RO | Bitfield 16 | N/ A | 1 | 5000 9 | 1
157 | Alarm 11 |  | RO | Bitfield 16 | N/ A | 1 | 5001 0 | 1
158 | Alarm 12 |  | RO | Bitfield 16 | N/ A | 1 | 5001 1 | 1
159 | Alarm 13 |  | RO | Bitfield 16 | N/ A | 1 | 5001 2 | 1
160 | Alarm 14 |  | RO | Bitfield 16 | N/ A | 1 | 5001 3 | 1
161 | Alarm 15 |  | RO | Bitfield 16 | N/ A | 1 | 5001 4 | 1
162 | Alarm 16 |  | RO | Bitfield 16 | N/ A | 1 | 5001 5 | 1
163 | Alarm 17 |  | RO | Bitfield 16 | N/ A | 1 | 5001 6 | 1

## Table 4
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 | 50000 | 1 | Abnormal String 1 | 106 | 1
2 | 50000 | 2 | Abnormal String 2 | 107 | 1
3 | 50000 | 3 | Abnormal String 3 | 108 | 1
4 | 50000 | 4 | Abnormal String 4 | 109 | 1
5 | 50000 | 5 | Abnormal String 5 | 110 | 1
6 | 50000 | 6 | Abnormal String 6 | 111 | 1
7 | 50000 | 10 | Software Ver. Unmatch | 504 | 1
8 | 50000 | 12 | Upgrade Failed | 505 | 1
9 | 50000 | 13 | Flash Fault | 61440 | 1
10 | 50000 | 14 | License Expired | 506 | 1
11 | 50001 | 1 | Software Ver. Unmatch | 504 | 2
12 | 50001 | 2 | Software Ver. Unmatch | 504 | 3
13 | 50001 | 3 | System Fault | 400 | 1
14 | 50001 | 4 | System Fault | 400 | 27
15 | 50001 | 5 | Abnormal DC Circuit | 200 | 16
16 | 50001 | 6 | Abnormal Inv. Circuit | 202 | 20
17 | 50001 | 7 | Abn. Residual Curr. | 318 | 1
18 | 50001 | 8 | Overtemperature | 321 | 1
19 | 50001 | 10 | System Fault | 400 | 28
20 | 50001 | 11 | Fan Fault | 320 | 1
21 | 50001 | 12 | Abnormal SPI Comm. | 322 | 1
22 | 50001 | 14 | System Fault | 400 | 29
23 | 50002 | 0 | Low Insulation Resistance | 313 | 1
24 | 50002 | 1 | AFCI Self-Check Failure | 411 | 1
25 | 50002 | 2 | DC Arc Fault | 412 | 1
26 | 50002 | 3 | AFCI Self-Check Failure | 411 | 2
27 | 50002 | 4 | AFCI Self-Check Failure | 411 | 3
28 | 50002 | 5 | Abnormal Inv. Circuit | 202 | 21
29 | 50002 | 7 | System Fault | 400 | 30
30 | 50002 | 8 | System Fault | 400 | 31
31 | 50002 | 9 | String 3 Reversed | 122 | 1
32 | 50002 | 12 | DC Arc Fault | 412 | 2
33 | 50002 | 13 | DC Arc Fault | 412 | 3
34 | 50002 | 14 | DC Arc Fault | 412 | 4
35 | 50002 | 15 | System Fault | 400 | 23
36 | 50003 | 1 | String 1 Reversed | 120 | 1
37 | 50003 | 2 | String 2 Reversed | 121 | 1
38 | 50003 | 3 | Abnormal DC Circuit | 200 | 12
39 | 50003 | 6 | String 4 Reversed | 123 | 1
40 | 50003 | 7 | String 5 Reversed | 124 | 1
41 | 50003 | 8 | String 6 Reversed | 125 | 1
42 | 50003 | 9 | High DC Input Voltage | 103 | 1
43 | 50003 | 10 | High DC Input Voltage | 103 | 2
44 | 50003 | 11 | High DC Input Voltage | 103 | 3
45 | 50003 | 12 | High DC Input Voltage | 103 | 4
46 | 50003 | 15 | Abnormal DC Circuit | 200 | 15
47 | 50004 | 2 | String 1 Reversed | 120 | 2
48 | 50004 | 3 | String 2 Reversed | 121 | 2
49 | 50004 | 4 | String 7 Reversed | 126 | 1
50 | 50004 | 5 | String 7 Reversed | 126 | 2
51 | 50004 | 6 | String 8 Reversed | 127 | 1
52 | 50004 | 7 | String 8 Reversed | 127 | 2
53 | 50004 | 8 | Abnormal PV String Connection | 413 | 1
54 | 50004 | 9 | Abnormal PV String Connection | 413 | 2
55 | 50004 | 10 | Abnormal PV String Connection | 413 | 3
56 | 50004 | 11 | Abnormal PV String Connection | 413 | 4
57 | 50004 | 12 | String 3 Reversed | 122 | 2
58 | 50004 | 13 | String 4 Reversed | 123 | 2
59 | 50004 | 14 | String 5 Reversed | 124 | 2
60 | 50004 | 15 | String 6 Reversed | 125 | 2
61 | 50005 | 1 | Abnormal DC Circuit | 200 | 3
62 | 50005 | 2 | Abn. Auxiliary Power | 410 | 4
63 | 50005 | 4 | Abnormal DC Circuit | 200 | 10
64 | 50005 | 5 | Abnormal DC Circuit | 200 | 11
65 | 50005 | 6 | Abnormal DC Circuit | 200 | 30
66 | 50005 | 7 | BST Inductor Cable Connection Abnormal | 414 | 1
67 | 50005 | 8 | BST Inductor Cable Connection Abnormal | 414 | 2
68 | 50005 | 9 | BST Inductor Cable Connection Abnormal | 414 | 3
69 | 50005 | 10 | BST Inductor Cable Connection Abnormal | 414 | 4
70 | 50006 | 6 | System Fault | 400 | 3
71 | 50006 | 10 | Abnormal Inv. Circuit | 202 | 13
72 | 50006 | 12 | Abnormal Inv. Circuit | 202 | 14
73 | 50007 | 1 | Abnormal Inv. Circuit | 202 | 16
74 | 50007 | 5 | System Fault | 400 | 21
75 | 50008 | 0 | Abnormal Grid Voltage | 301 | 4
76 | 50008 | 3 | Abnormal Grid Voltage | 301 | 16
77 | 50008 | 6 | Abnormal Grid Frequency | 305 | 2
78 | 50008 | 7 | Abnormal Grid Frequency | 305 | 4
79 | 50008 | 8 | Abnormal Grid Voltage | 301 | 28
80 | 50008 | 9 | Abnormal Grid Voltage | 301 | 29
81 | 50008 | 10 | Abnormal Grounding | 326 | 1
82 | 50008 | 11 | Abnormal Grid Voltage | 301 | 26
83 | 50008 | 12 | Abnormal Grid Frequency | 305 | 5
84 | 50009 | 0 | Abnormal Grid Voltage | 301 | 31
85 | 50009 | 1 | Abnormal Grid Voltage | 301 | 32
86 | 50009 | 2 | Abnormal Grid Voltage | 301 | 33
87 | 50009 | 8 | Abnormal Grid Voltage | 301 | 19
88 | 50016 | 0 | Abnormal String 1 | 106 | 1
89 | 50016 | 1 | Abnormal String 2 | 107 | 1
90 | 50016 | 2 | Abnormal String 3 | 108 | 1
91 | 50016 | 3 | Abnormal String 4 | 109 | 1
92 | 50016 | 4 | Abnormal String 5 | 110 | 1
93 | 50016 | 5 | Abnormal String 6 | 111 | 1
94 | 50016 | 6 | Abnormal String 7 | 112 | 1
95 | 50016 | 7 | Abnormal String 8 | 113 | 1

## Table 5
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 | Active power control mode | RW | U16 |  | 1 | 40118 | 1 | Stores data but does not support high- frequency write operations.
2 | Active power percentage derating (1%) | RW | U16 | % | 1 | 40119 | 1
3 | Fixed active power derating | RW | U16 | kW | 10 | 40120 | 1

## Table 6
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
4 | Active power change gradient | RW | U16 | %/s | 10 | 40121 | 1
5 | Active power percentage derating (0.1%) | RW | U16 | % | 10 | 40125 | 1
6 | Active power percentage derating command (0.1%) | WO | U16 | % | 10 | 40232 | 1 | Supports high- frequency write operations but does not store data.
7 | Active power percentage derating command (1%) | WO | U16 | % | 1 | 40234 | 1
8 | Fixed active power derating command | WO | U16 | kW | 10 | 40235 | 1

## Table 7
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 | Reactive power compensation | RW | U16 |  | 1 | 40117 | 1 | Stores data but does not support high-

## Table 8
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
2 | Reactive power compensation (PF) | RW | I16 |  | 1000 | 40122 | 1 | frequency write operations.
3 | Reactive power compensation (Q/S) | RW | I16 |  | 1000 | 40123 | 1
4 | Reactive power adjustment time | RW | U16 | s | 1 | 40124 | 1
5 | Reactive power compensation command (Q/S) | WO | I16 |  | 1000 | 40236 | 1 | Supports high- frequency write operations but does not store data.
6 | Reactive power compensation command (PF) | WO | I16 |  | 1000 | 40237 | 1

## Table 9
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 |  | [2, 10]
10 | % | [0, 100]
1000 |  | (–1, –0.8]U[0.8, 1]
10 | % | [0, 100]
1000 |  | (–1, –0.8]U[0.8, 1]
10 | % | [0, 100]
1000 |  | (–1, –0.8]U[0.8, 1]
10 | % | [0, 100]
1000 |  | (–1, –0.8]U[0.8, 1]
10 | % | [0, 100]
1000 |  | (–1, –0.8]U[0.8, 1]
10 | % | [0, 100]
1000 |  | (–1, –0.8]U[0.8, 1]
10 | % | [0, 100]
1000 |  | (–1, –0.8]U[0.8, 1]
10 | % | [0, 100]
1000 |  | (–1, –0.8]U[0.8, 1]
10 | % | [0, 100]
1000 |  | (–1, –0.8]U[0.8, 1]
10 | % | [0, 100]
1000 |  | (–1, –0.8]U[0.8, 1]

## Table 10
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 |  | [2, 10]
10 | % | [80, 136]
1000 |  | [–0.6, 0.6]
10 | % | [80, 136]
1000 |  | [–0.6, 0.6]
10 | % | [80, 136]
1000 |  | [–0.6, 0.6]
10 | % | [80, 136]
1000 |  | [–0.6, 0.6]
10 | % | [80, 136]
1000 |  | [–0.6, 0.6]
10 | % | [80, 136]
1000 |  | [–0.6, 0.6]
10 | % | [80, 136]

## Table 12
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
0 |  | VDE-AR-N-4105 | Germany
1 |  | NB/T 32004 | China
2 |  | UTE C 15-712-1(A) | France
3 |  | UTE C 15-712-1(B) | France
4 |  | UTE C 15-712-1(C) | France
5 |  | VDE 0126-1-1-BU | Bulgaria
6 |  | VDE 0126-1-1-GR(A) | Greece
7 |  | VDE 0126-1-1-GR(B) | Greece
8 |  | BDEW-MV | Germany
9 |  | G59-England | UK
10 |  | G59-Scotland | UK
11 |  | G83-England | UK
12 |  | G83-Scotland | UK
13 |  | CEI0-21 | Italy
14 |  | EN50438-CZ | Czech Republic
15 |  | RD1699/661 | Spain
16 |  | RD1699/661-MV480 | Spain
17 |  | EN50438-NL | Netherlands
18 |  | C10/11 | Belgium
19 |  | AS4777 | Australia
20 |  | IEC61727 | General
21 |  | Custom (50 Hz) | Custom
22 |  | Custom (60 Hz) | Custom
23 |  | CEI0-16 | Italy
24 |  | CHINA-MV480 | China
25 |  | CHINA-MV | China
26 |  | TAI-PEA | Thailand
27 |  | TAI-MEA | Thailand
28 |  | BDEW-MV480 | Germany
29 |  | Custom MV480 (50 Hz) | Custom
30 |  | Custom MV480 (60 Hz) | Custom
31 |  | G59-England-MV480 | UK
32 |  | IEC61727-MV480 | General
33 |  | UTE C 15-712-1-MV480 | France
34 |  | TAI-PEA-MV480 | Thailand
35 |  | TAI-MEA-MV480 | Thailand
36 |  | EN50438-DK-MV480 | Denmark
37 |  | Japan standard (50 Hz) | Japan
38 |  | Japan standard (60 Hz) | Japan
39 |  | EN50438-TR-MV480 | Turkey
40 |  | EN50438-TR | Turkey
41 |  | C11/C10-MV480 | Belgium
42 |  | Philippines | Philippines
43 |  | Philippines-MV480 | Philippines
44 |  | AS4777-MV480 | Australia
45 |  | NRS-097-2-1 | South Africa
46 |  | NRS-097-2-1-MV480 | South Africa
47 |  | KOREA | South Korea
48 |  | IEEE 1547-MV480 | USA
49 |  | IEC61727-60Hz | General
50 |  | IEC61727-60Hz-MV480 | General
51 |  | CHINA_MV500 | China
52 |  | ANRE | Romania
53 |  | ANRE-MV480 | Romania
54 |  | ELECTRIC RULE NO.21-MV480 | California, USA
55 |  | HECO-MV480 | Hawaii, USA
56 |  | PRC_024_Eastern-MV480 | Eastern USA
57 |  | PRC_024_Western-MV480 | Western USA
58 |  | PRC_024_Quebec-MV480 | Quebec, Canada
59 |  | PRC_024_ERCOT-MV480 | Texas, USA
60 |  | PO12.3-MV480 | Spain
61 |  | EN50438_IE-MV480 | Ireland
62 |  | EN50438_IE | Ireland
63 |  | IEEE 1547a-MV480 | USA
64 |  | Japan standard (MV420-50 Hz) | Japan
65 |  | Japan standard (MV420-60 Hz) | Japan
66 |  | Japan standard (MV440-50 Hz) | Japan
67 |  | Japan standard (MV440-60 Hz) | Japan
68 |  | IEC61727-50Hz-MV500 | General
70 |  | CEI0-16-MV480 | Italy
71 |  | PO12.3 | Spain
72 |  | Japan standard (MV400-50 Hz) | Japan
73 |  | Japan standard (MV400-60 Hz) | Japan
74 |  | CEI0-21-MV480 | Italy
75 |  | KOREA-MV480 | South Korea
76 |  | Egypt ETEC | Egypt
77 |  | Egypt ETEC-MV480 | Egypt
78 |  | CHINA_MV800 | China
79 |  | IEEE 1547-MV600 | USA
80 |  | ELECTRIC RULE NO.21-MV600 | California, USA
81 |  | HECO-MV600 | Hawaii, USA
82 |  | PRC_024_Eastern-MV600 | Eastern USA
83 |  | PRC_024_Western-MV600 | Western USA
84 |  | PRC_024_Quebec-MV600 | Quebec, Canada
85 |  | PRC_024_ERCOT-MV600 | Texas, USA
86 |  | IEEE 1547a-MV600 | USA
87 |  | EN50549-LV | Ireland
88 |  | EN50549-MV480 | Ireland
89 |  | Jordan-Transmission | Jordan
90 |  | Jordan-Transmission-MV480 | Jordan
91 |  | NAMIBIA | Namibia
92 |  | ABNT NBR 16149 | Brazil
93 |  | ABNT NBR 16149-MV480 | Brazil
94 |  | SA_RPPs | South Africa
95 |  | SA_RPPs-MV480 | South Africa
96 |  | INDIA | India
97 |  | INDIA-MV500 | India
98 |  | ZAMBIA | Zambia
99 |  | ZAMBIA-MV480 | Zambia
100 |  | Chile | Chile
101 |  | Chile-MV480 | Chile
102 |  | CHINA-MV500-STD | China
103 |  | CHINA-MV480-STD | China
104 |  | Mexico-MV480 | Mexico
105 |  | Malaysian | Malaysia
106 |  | Malaysian-MV480 | Malaysia
107 |  | KENYA_ETHIOPIA | East Africa
108 |  | KENYA_ETHIOPIA-MV480 | East Africa
109 |  | G59-England-MV800 | UK
110 |  | NIGERIA | Nigeria
111 |  | NIGERIA-MV480 | Nigeria
112 |  | DUBAI | Dubai
113 |  | DUBAI-MV480 | Dubai
114 |  | Northern Ireland | Northern Ireland
115 |  | Northern Ireland-MV480 | Northern Ireland
116 |  | Cameroon | Cameroon
117 |  | Cameroon-MV480 | Cameroon
118 |  | Jordan-Distribution | Jordan
119 |  | Jordan-Distribution-MV480 | Jordan
120 |  | Custom-MV600-50Hz | Custom
121 |  | AS4777-MV800 | Australia
122 |  | INDIA-MV800 | India
123 |  | IEC61727-MV800 | General
124 |  | BDEW-MV800 | Germany
125 |  | ABNT NBR 16149-MV800 | Brazil
126 |  | UTE C 15-712-1-MV800 | France
127 |  | Chile-MV800 | Chile
128 |  | Mexico-MV800 | Mexico
129 |  | EN50438-TR-MV800 | Turkey
130 |  | TAI-PEA-MV800 | Thailand
131 |  | Philippines-MV800 | Philippines
132 |  | Malaysian-MV800 | Malaysia
133 |  | NRS-097-2-1-MV800 | South Africa
134 |  | SA_RPPs-MV800 | South Africa
135 |  | Jordan-Transmission-MV800 | Jordan
136 |  | Jordan-Distribution-MV800 | Jordan
137 |  | Egypt ETEC-MV800 | Egypt
138 |  | DUBAI-MV800 | Dubai
139 |  | SAUDI-MV800 | Saudi Arabia
140 |  | EN50438_IE-MV800 | Ireland
141 |  | EN50549-MV800 | Ireland
142 |  | Northern Ireland-MV800 | Northern Ireland
143 |  | CEI0-21-MV800 | Italy
144 |  | IEC 61727-MV800-60Hz | General
145 |  | NAMIBIA_MV480 | Namibia
146 |  | Japan (LV202-50 Hz) | Japan
147 |  | Japan (LV202-60 Hz) | Japan
148 |  | Pakistan-MV800 | Pakistan
149 |  | BRASIL-ANEEL-MV800 | Brazil
150 |  | Israel-MV800 | Israel
151 |  | CEI0-16-MV800 | Italy
152 |  | ZAMBIA-MV800 | Zambia
153 |  | KENYA_ETHIOPIA-MV800 | East Africa
154 |  | NAMIBIA_MV800 | Namibia
155 |  | Cameroon-MV800 | Cameroon
156 |  | NIGERIA-MV800 | Nigeria
157 |  | ABUDHABI-MV800 | Abu Dhabi
158 |  | LEBANON | Lebanon
159 |  | LEBANON-MV480 | Lebanon
160 |  | LEBANON-MV800 | Lebanon
161 |  | ARGENTINA-MV800 | Argentina
162 |  | ARGENTINA-MV500 | Argentina
163 |  | Jordan-Transmission-HV | Jordan
164 |  | Jordan-Transmission-HV480 | Jordan
165 |  | Jordan-Transmission-HV800 | Jordan
166 |  | TUNISIA | Tunisia
167 |  | TUNISIA-MV480 | Tunisia
168 |  | TUNISIA-MV800 | Tunisia
169 |  | JAMAICA-MV800 | Jamaica
170 |  | AUSTRALIA-NER | Australia
171 |  | AUSTRALIA-NER-MV480 | Australia
172 |  | AUSTRALIA-NER-MV800 | Australia
173 |  | SAUDI | Saudi Arabia
174 |  | SAUDI-MV480 | Saudi Arabia
175 |  | Ghana-MV480 | Ghana
176 |  | Israel | Israel
177 |  | Israel-MV480 | Israel
178 |  | Chile-PMGD | Chile
179 |  | Chile-PMGD-MV480 | Chile
180 |  | VDE-AR-N4120-HV | Germany
181 |  | VDE-AR-N4120-HV480 | Germany
182 |  | VDE-AR-N4120-HV800 | Germany
183 |  | IEEE 1547-MV800 | USA
184 |  | Nicaragua-MV800 | Nicaragua
185 |  | IEEE 1547a-MV800 | USA
186 |  | ELECTRIC RULE NO.21-MV800 | California, USA
187 |  | HECO-MV800 | Hawaii, USA
188 |  | PRC_024_Eastern-MV800 | Eastern USA
189 |  | PRC_024_Western-MV800 | Western USA
190 |  | PRC_024_Quebec-MV800 | Quebec, Canada
191 |  | PRC_024_ERCOT-MV800 | Texas, USA
192 |  | Custom-MV800-50Hz | Custom
193 |  | RD1699/661-MV800 | Spain
194 |  | PO12.3-MV800 | Spain
195 |  | Mexico-MV600 | Mexico
196 |  | Vietnam-MV800 | Vietnam
197 |  | CHINA-LV220/380 | China
198 |  | SVG-LV | Dedicated
199 |  | Vietnam | Vietnam
200 |  | Vietnam-MV480 | Vietnam
201 |  | Chile-PMGD-MV800 | Chile
202 |  | Ghana-MV800 | Ghana
203 |  | TAIPOWER | Taiwan
204 |  | TAIPOWER-MV480 | Taiwan
205 |  | TAIPOWER-MV800 | Taiwan
206 |  | IEEE 1547-LV208 | USA
207 |  | IEEE 1547-LV240 | USA
208 |  | IEEE 1547a-LV208 | USA
209 |  | IEEE 1547a-LV240 | USA
210 |  | ELECTRIC RULE NO.21-LV208 | USA
211 |  | ELECTRIC RULE NO.21-LV240 | USA
212 |  | HECO-O+M+H-LV208 | USA
213 |  | HECO-O+M+H-LV240 | USA
214 |  | PRC_024_Eastern-LV208 | USA
215 |  | PRC_024_Eastern-LV240 | USA
216 |  | PRC_024_Western-LV208 | USA
217 |  | PRC_024_Western-LV240 | USA
218 |  | PRC_024_ERCOT-LV208 | USA
219 |  | PRC_024_ERCOT-LV240 | USA
220 |  | PRC_024_Quebec-LV208 | USA
221 |  | PRC_024_Quebec-LV240 | USA
222 |  | ARGENTINA-MV480 | Argentina
223 |  | Oman | Oman
224 |  | Oman-MV480 | Oman
225 |  | Oman-MV800 | Oman
226 |  | Kuwait | Kuwait
227 |  | Kuwait-MV480 | Kuwait
228 |  | Kuwait-MV800 | Kuwait
229 |  | Bangladesh | Bangladesh
230 |  | Bangladesh-MV480 | Bangladesh
231 |  | Bangladesh-MV800 | Bangladesh
232 |  | Chile-Net_Billing | Chile
233 |  | EN50438-NL-MV480 | Netherlands
234 |  | Bahrain | Bahrain
235 |  | Bahrain-MV480 | Bahrain
236 |  | Bahrain-MV800 | Bahrain
238 |  | Japan-MV550-50Hz | Japan
239 |  | Japan-MV550-60Hz | Japan
241 |  | ARGENTINA | Argentina
242 |  | KAZAKHSTAN-MV800 | Kazakhstan
243 |  | Mauritius | Mauritius
244 |  | Mauritius-MV480 | Mauritius
245 |  | Mauritius-MV800 | Mauritius
246 |  | Oman-PDO-MV800 | Oman
247 |  | EN50438-SE | Sweden
248 |  | TAI-MEA-MV800 | Thailand
249 |  | Pakistan | Pakistan
250 |  | Pakistan-MV480 | Pakistan
251 |  | PORTUGAL-MV800 | Portugal
252 |  | HECO-L+M-LV208 | USA
253 |  | HECO-L+M-LV240 | USA
254 |  | C10/11-MV800 | Belgium
255 |  | Austria | Austria
256 |  | Austria-MV480 | Austria
257 |  | G98 | UK
258 |  | G99-TYPEA-LV | UK
259 |  | G99-TYPEB-LV | UK
260 |  | G99-TYPEB-HV | UK
261 |  | G99-TYPEB-HV-MV480 | UK
262 |  | G99-TYPEB-HV-MV800 | UK
263 |  | G99-TYPEC-HV-MV800 | UK
264 |  | G99-TYPED-MV800 | UK
265 |  | G99-TYPEA-HV | UK
266 |  | CEA-MV800 | India
267 |  | EN50549-MV400 | Europe
268 |  | VDE-AR-N4110 | Germany
269 |  | VDE-AR-N4110-MV480 | Germany
270 |  | VDE-AR-N4110-MV800 | Germany
271 |  | Panama-MV800 | Panama
272 |  | North Macedonia-MV800 | North Macedonia
273 |  | NTS | Spain
274 |  | NTS-MV480 | Spain
275 |  | NTS-MV800 | Spain

## Table 13
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 |  | [0, 10]
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1000
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1000 | ... | ...
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1000

## Table 14
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 |  | [0, 10]
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1 | W | [Discharging power limit, Charging power limit]. For details, see the description of the supported model.
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1 | W ... | [Discharging power limit, Charging power limit]. For details, see the description of the supported model. ...
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1 | min | [0, 1440]. The value is the elapsed minutes since 00:00 a.m. The start time should be earlier than the end time.
1 | W | [Discharging power limit, Charging power limit]. For details, see the description of the supported model.

## Table 15
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
0 | 1–247 | 248–255

## Table 16
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
2 | Matching identifier between a request frame and a response frame | Assigned by the client; better be unique for each data frame | The identifier of the response frame from the server must be consistent with that of the request frame.
2 | 0 = Modbus protocol | Assigned by the client; 0 by default | The identifier of the response frame from the server must be consistent with that of the request frame.
2 | Follow-up data length | Assigned by the client based on the actual data frame | Assigned by the server based on the actual frame length
1 | 0 | Assigned by the client based on the actual data frame request | The identifier of the response frame from the server must be consistent with that of the request frame.

## Table 19
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 |  | 0x03
2 |  | 0x0000–0xFFFF
2 |  | 1–125 Description
1 |  | 0x03
1 |  | 2 x N Description
1 |  | 0x83
1 |  | See Exception Code List.

## Table 20
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
0
1
0
0
0
6
0
3
32
0
2
0
1
0
0
0
7
0
3
4
0
0
0
1

## Table 21
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
0
1
0
0
0
3
0
83
3
1 | 0x06
2 | 0x0000–0xFFFF
2 | 0x0000–0xFFFF Description
1 | 0x06
2 | 0x0000–0xFFFF
2 | 0x0000–0xFFFF Description
1 | 0x86

## Table 22
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 | See Exception Code List. Frame Data
0
1
0
0
0
6
0
6
8
0
0
0
1
0
0
0
6
0
6
8
0
0

## Table 23
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
0
1
0
0
0
3
0
86
4
1 | 0x10
2 | 0x0000–0xFFFF
2 | 0x0000–0x007b
1 | 2 x N Value

## Table 24
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 | 0x10
2 | 0x0000–0xFFFF
2 | 0x0000–0x007b Description
1 | 0x90
1 | See Exception Code List. Frame Data
0
1
0
0
0
0
10
0
2
4
0

## Table 25
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
2
0
32
0
1
0
0
0
6
0
10
0
2
0
1
0
0
0
3
0
90
4

## Table 28
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 |  |  | 0xAB
1 |  |  | See Exception Code List. Description
1 |  |  | 0x2B
1 |  |  | 0x0E
1 |  |  | 3
1 | Object ID | Length (Byte) 1 1 1 1 1 1 1 1 | 0x87 | Description 0x2B 0x0E 3 3 - - - 0x87

## Table 30
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 | Device model |  | ASCII character string | SUN2000
2 | Device software version |  | ASCII character string | -
3 | Port protocol version |  | ASCII character string | See the interface protocol version definitions.
4 | ESN |  | ASCII character string | -
5 | Device ID |  | int | 0, 1, 2, 3,... (assigned by NEs; 0 indicates the master device into which the Modbus card is inserted)
6 | Feature version | Length (Byte) | ASCII character string | - | Description
1 |  |  | 0xAB
1 |  |  | See Exception Code List.

## Table 31
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 | 0x41
1 | 0x05
1 | 1 + N
1 | Unique ID of a file -

## Table 32
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 |  | 0x41
1 |  | 0x05
1 |  | 6 + N
1 |  | Unique ID of a file
4 |  | -
1 | Length (Byte) | - - | Description
1 |  | 0xC1
1 |  | See Exception Code List. Description
1 |  | 0x41
1 |  | 0x06

## Table 33
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 | 3
1 | Unique ID of a file
2 | 0x0000–0xFFFF Description
1 | 0x41
1 | 0x06
1 | 3 + N
1 | -
2 | 0x0000–0xFFFF - Description
1 | 0xC1
1 | See Exception Code List. Description
1 | 0x41
1 | 0x0c
1 | 1
1 | -

## Table 34
No | Signal name | Read and write | Type | Unit | Gain | Address | Number of regs | Scope
1 | 0x41
1 | 0x0c
1 | 3
1 | -
2 | - Description
1 | 0xC1
1 | See Exception Code List. | Restraints 10s 10s 6 10s